## Grand Summary
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
WORKS FOR CONSTRUCTION OF GASPA, MUTUNDA AND NYAKABAALE SOLAR POWERED PIPED WATER SUPPLY AND SANITATION SYSTEMS IN KIRYANDONGO REFUGEE HOSTING DISTRICT
PROCUREMENT REFERENCE NUMBER: MWE/WRKS/22-23/00005
Grand Summary
Bill No | Description | Investment Costs
UShs
GENERAL
KIR G-1 | General Items | 90000000
KIR G-2 | Dayworks | 0
| Sub Total for General Items | 90000000
GASPA RGC
WATER SUPPLY AND EQUIPMENT
GPA W-1 | Borehole Pump Station (DWD 77381) | 0
GPA W-2 | Borehole Pump Station (DWD 77380) | 0
GPA W-3 | Borehole Pumping Mains (DWD 77380) | 0
GPA W-4 | Storage Reservoir and Site Works | 0
GPA W-5 | Distribution Network | 0
GPA W-6 | Intensification Network | 0
GPA W-7 | Chemical House (1No.) | 0
GPA W-8 | Borehole Guard / Attendant House (1No.) | 0
GPA W-9 | Water Office Block | 0
GPA ME-1 | Mechanical & Electrical Works (DWD 77381) | 0
GPA ME-2 | Mechanical & Electrical Works (Water Office) | 0
GPA ME-3 | Mechanical & Electrical Works (Chemical House - 1No.) | 0
GPA ME-4 | Tools and Equipment | 0
SANITATION
GPA S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
GPA S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
GPA S-3 | 4 Stance Waterborne Toilet - 2No. | 0
| Sub Total for Gaspa WSS | 0
NYAKABALE RGC
WATER SUPPLY AND EQUIPMENT
NYA W-1 | Borehole Pump Station (DWD 77382) | 0
NYA W-2 | Borehole Pump Station (DWD 77383) | 0
NYA W-3 | Borehole Pumping Mains (DWD 77382) | 0
NYA W-4 | Borehole Pumping Mains (DWD 77383) | 0
NYA W-5 | Storage Reservoir and Site Works | 0
NYA W-6 | Distribution Network | 0
NYA W-7 | Intensification Network | 0
NYA W-8 | Chemical House (1No.) | 0
NYA W-9 | Borehole Guard / Attendant House (2No.) | 0
NYA W-10 | Water Office Block | 0
NYA ME-1 | Mechanical & Electrical Works (DWD 77382) | 30000000
NYA ME-2 | Mechanical & Electrical Works (DWD 77383) | 30000000
NYA ME-3 | Mechanical & Electrical Works (Water Office) | 0
NYA ME-4 | Mechanical & Electrical Works (Chemical House - 1No.) | 0
NYA ME-5 | Tools and Equipment | 0
SANITATION
NYA S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
NYA S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
NYA S-3 | 4 Stance Waterborne Toilet - 1No. | 0
| Sub Total for Nyakabale WSS | 60000000
MUTUNDA RGC
WATER SUPPLY AND EQUIPMENT
MUT W-1 | Borehole Pump Station (DWD 77378) | 0
MUT W-2 | Borehole Pump Station (DWD 77379) | 0
MUT W-3 | Borehole Pumping Mains (DWD 77378) to Popara West Reservoir | 0
MUT W-4 | Borehole Pumping Mains (DWD 77378) to Diima Reservoir | 0
MUT W-5 | Popara Reservoir Storage Reservoir and Site Works | 0
MUT W-6 | Popara West Distribution Network | 0
MUT W-7 | Popara West Intensification Network | 0
MUT W-8 | Teyago Storage Reservoir and Site Works | 0
MUT W-9 | Teyago Distribution Network | 0
MUT W-10 | Teyago Intensification Network | 0
MUT W-11 | Chemical House (2No.) | 0
MUT W-12 | Borehole Guard / Attendant House (1No.) | 0
MUT W-13 | Water Office Block | 0
MUT ME-1 | Mechanical & Electrical Works (DWD 77378) | 30000000
MUT ME-2 | Mechanical & Electrical Works (Water Office) | 0
MUT ME-3 | Mechanical & Electrical Works (Chemical House - 2No.) | 0
MUT ME-4 | Tools and Equipment | 0
SANITATION
MUT S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
MUT S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
MUT S-3 | 4 Stance Waterborne Toilet - 1No. | 0
| Sub Total for Mutunda WSS | 30000000
| Sub-Total 1 | 180000000
| Allow for 10% contingency | 18000000
| Sub-Total 2 | 198000000
| Allow for 18% VAT | 35640000
| GRAND TOTAL | 233640000

## KIR G-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
KIRYANDONGO THREE RGCs PIPED WATER SUPPLY AND SANITATION SYSTEMS
BILL No. KIR G-1
DESCRIPTION: GENERAL ITEMS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Contractual Requirements
A110.1 | Performance security clause | sum | 1 |  | 0
A110.2 | Advance payment guarantee | sum | 1 |  | 0
A120 | Insurance of works covering all installations during and up to 28 days after the end of the defects liability period | sum | 1 |  | 0
A130 | Third party insurance | sum | 1 |  | 0
A140 | Insurance of Contractors Equipment | sum | 1 |  | 0
Specified Requirements
Accommodation for the Project Manager's staff
A211.1 | Establishment and removal of offices for the Engineer's staff | sum | 1 |  | 0
A211.2 | Provision of rented office accommodation for the Engineer's staff before establishment of site offices | months | 3 |  | 0
A211.3 | Provision of rented (1No unit), 3 bedroomed residential accommodation house to the Engineers approval for the Engineer's and his/her staff | months | 15 |  | 0
A211.4 | Allow PC for rental charges for 1No. Junior Resident Engineer's staff residential accommodation of area not less than 150m2 in an approved location. | months | 15 |  | 0
A211.5 | Maintenance of offices for the Engineer's staff including provision and payment of utility services | months | 15 |  | 0
A214 | Maintenance of housing accommodation for the Engineer's staff (1No. Units) including provision and payment of utility services | months | 15 |  | 0
Services for the Project Manager's staff
Communication System as follows
A244.1 | Establish communication system | sum | 1 |  | 0
A244.2 | Maintenance of the communication system | months | 15 |  | 0
A244.3 | Provision of 3No. Mobile phone handsets for use by the Engineer and his staff | sum | 1 |  | 0
A244.4 | Payment of bills on mobile calls | months | 15 |  | 0
A244.5 | Provide and maintain 2No. 16megapixels DSLR digital cameras with 2No. 16GB memory card of approved make by the Engineer for the entire contract period | sum | 1 |  | 0
Equipment for use by the Project Manager's staff as per Specifications
Surveying Equipment
A255.1 | Use of Contractor's surveying equipment by the Engineer | months | 6 |  | 0
|  |  |  | Carried to Collection | 0
Office Equipment and House Equipment
A255.2 | Provision of House furniture & equipment | sum | 1 |  | 0
A255.3 | Provision of office furniture & equipment | sum | 1 |  | 0
A255.4 | Maintenance of office and House furniture & equipment | months | 1 |  | 0
A255.5 | Provision of office stationary and consumables | months | 15 |  | 0
A255.6 | Provision for purchase of 2no pick-up, double cabin, 4WD, air conditioned, diesel engine, as approved by the Engineer in accordance with Specification Clause 10.12.1 including registration and licencing. | nr | 2 |  | 0
A255.7 | Running costs in accordance with the specifications Clause 10.12.2 for the vehicle above, up to 4,000km per month | veh-month | 30 |  | 0
A255.8 | Provision of Motorcyles of Capacity 125 C.C for use by Client Trainees | nr | 3 |  | 0
A420.9 | Running costs in accordance with the specifications for the cycles above, up to 1,000km per month | cyc-month | 60 |  | 0
Laboratory Equipment
A266 | Provision of concrete, aggregate and soils testing equipment | months | 12 |  | 0
Attendance upon the Project Manager's staff
A268.1 | Provision of the services of Office Assistants | months | 15 |  | 0
A268.2 | Provision of the services of a permanent driver for use by project manager | months | 15 |  | 0
A268.3 | Provision of the services of survey chainmen | months | 7 |  | 0
Testing works
Testing of Materials
A270.1 | Testing of pipes at Uganda Bureau of Standards | sum | 1 |  | 0
A270.2 | Testing of concrete works test cubes at Ministry of Works Materials Laboratories | sum | 1 |  | 0
A280.1 | Testing and certification of mechanical and electrical systems | sum | 1 |  | 0
A280.2 | Pressure testing of and sterilisation of water mains as per specifications: nominal bore not exceeding 500mm; maximum test pressure not exceeding twice the pipe's pressure rating. | km | 97 |  | 0
A280.3 | Water tightedness tests for all water retaining structures and reservoirs | sum | 1 |  | 0
A280.4 | Test running of water supply system, inclusive of full operations of the water supply system for 30 consecutive days, preparation of daily reports on the operations that comprise of the amount of water pumped, quantity of chemicals utilised, hours of pumping, energy consumed, at least 6No off site detailed water quality tests etc as directed by the Engineer. These shall form part of the operation and maintenance manual and As-Built drawings that shall be submitted by the Contractor to the Employer. Training Private Operator's staff in basic operation and maintenance procedures of all plant and equipment supplied as per the technical specifications and to the Engineer's approval shall form part of this activity | sum | 1 |  | 0
0
A280.5 | Production of Operation and maintenance manuals and As-Built drawings to the satifisfaction of the Project Manager | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Temporary Works
A289.1 | Establishment & removal of site sign-boards (double sided/faced) at an agreed location with the engineer | nr | 4 |  | 0
A289.2 | Maintenance of site sign-boards until the issue of the Taking-over Certificate | month | 15 |  | 0
A289.3 | Provision for work in water affected areas, including dewatering of sites and work areas, all temporary works, protection, access, etc to ensure the works are completed as specified; include removal of facilities. | sum | 1 |  | 0
A289.4 | Supply and installation of 450 x 800mm granite "Project Label Plates" made of engraved granite on the various installations as directed by the Engineer. | nr | 4 |  | 0
Provisional Sums
A420.1 | Allow for relocation of existing services including repair of damage caused to all existing services (e.g. pipes, cables, drains, e.t.c) | sum | 1 | 30000000 | 30000000
0
A420.2 | Provision for carrying out joint setting out of works (building and water) by the contractor, spearheaded by the consulatnt and client representatives incuding the cost of necessary rental equipment as applicable before commencement. | sum | 1 | 30000000 | 30000000
0
A420.3 | Allow for tunnel boring under main highway to lay pipework; including all associated costs | sum | 1 | 30000000 | 30000000
A420.4 | Contractor's charges and profits associated with administration of Bill items A420.1 to A420.18 | % |  |  | 0
Occupational Health and Safety
A900 | Compliance with Health and Safety provisions as per Clause 1.45 (a) and 1.45(b) of the Technical Specifications on all three sites of Nyakabaale, Mutunda and Gaspa | sum | 1 |  | 0
Environmental, Social Safe Guards and Source Protection
Compliance with Environmental and Social Management Plan as per contractor's roles stipulated in Clause 1.49 of the technical specifications and listed below;
GASPA-ESS
A900.1 | Detect and remedy soil deposition in wetlands located in the project area | sum | 1 |  | 0
A900.2 | Allow for waste management including legal disposal | sum
A900.3 | Allow for monthly assessment of water quality, air quality and noise pollution. | months | 12 |  | 0
A900.4 | Allow for management of GBV cases as specified in ESMP | sum | 1 |  | 0
A900.5 | Allow for acquisition of permits; Waste Disposal from NEMA, Water abstraction permit from DWRM, Regulated activity in wetlands from NEMA, workplace registration permit from MOGLSD | sum | 1 |  | 0
A900.6 | Approval for campsites and Hoarding areas by Kiryandongo DLG | sum | 1 |  | 0
A900.7 | Allow for Development of Contractors ESMP | sum | 1 |  | 0
GASPA-SPP
Restoration of degraded areas
B900.1 | Support 2 farmers with incentives for Farmer Managed Natural Regeneration (FMNR) around 2 water sources covering at least 2 acres. | FMNR Sites | 2 |  | 0
B900.2 | Restore indigenous trees by planting 500 tree seedlings of Omukoko (Pterygota mildbraedii) and Omutuba (Ficus nantalensis). | trees | 500 |  | 0
| Carried to Collection |  |  |  | 90000000
0
| Reforestation of woodlands, grassland, forested areas |  |  |  | 0
B900.3 | Plant 5 acres of bamboo in gullies (soil erosion sites) | acres | 5 |  | 0
B900.4 | Establish tree seedling nursery bed | Tree Nursery | 1 |  | 0
B900.5 | Distribute 2,000 fruit tree seedlings (Mangoes, Ovacado, Neem, Orange, Moringa, other multipurpose trees, medicinal or ornamental plants) | tree seedlings | 2000 |  | 0
B900.6 | Plant 2 acres of woodlots | acres | 2 |  | 0
B900.7 | Uproot / cut down invasive species of trees, grass, shrub & thicket | acres | 0.5 |  | 0
0
| Promote better sanitation and hygiene practices around sources |  |  |  | 0
C900.1 | Support 10 households to construct lined pit latrines near production wells | HHs | 10 |  | 0
Support selected community groups in climate smart agriculture (CSA) practices
D900.1 | Support 2 farmer groups in soil and water conservation technologies e.g., contours, mulching, micro irrigation. | Groups | 2 |  | 0
D900.2 | Plant soil conservation tree species in household | HHs | 20 |  | 0
NYAKABAALE-ESS
A900.1 | Detect and remedy soil deposition in wetlands located in the project area | sum | 1 |  | 0
A900.2 | Allow for waste management including legal disposal | sum | 1 |  | 0
A900.3 | Allow for monthly assessment of water quality, air quality and noise pollution. | months | 12 |  | 0
A900.4 | Allow for management of GBV cases as specified in ESMP | sum | 1 |  | 0
A900.5 | Allow for acquisition of permits; Waste Disposal from NEMA, Water abstraction permit from DWRM, Regulated activity in wetlands from NEMA, workplace registration permit from MOGLSD | sum | 1 |  | 0
A900.6 | Allow for acquisition of permits for Highway crossing from UNRA | sum | 1 |  | 0
A900.7 | Approval for campsites and Hoarding areas by Kiryandongo DLG | sum | 1 |  | 0
A900.8 | Allow for Development of Contractors ESMP | sum | 1 |  | 0
0
NYAKABAALE-SPP
Restoration of degraded areas
B900.1 | Support 2 farmers with incentives for Farmer Managed Natural Regeneration (FMNR) around 2 water sources covering at least 2 acres. | FMNR Sites | 2 |  | 0
B900.2 | Restore indigenous trees by planting 200 tree seedlings of Omukoko (Pterygota mildbraedii) and Omutuba (Ficus nantalensis). | trees | 200 |  | 0
Reforestation of woodlands, grassland, forested areas
B900.3 | Plant 4 acres of bamboo in gullies (soil erosion sites) | acres | 4 |  | 0
B900.4 | Establish tree seedling nursery bed at Mutunda SC Hqtrs (Site already in place | Tree Nursery | 1 |  | 0
B900.5 | Distribute 1,000 fruit tree seedlings (Mangoes, Ovacado, Neem, Orange, Moringa, other multipurpose trees, medicinal or ornamental plants) | tree seedlings | 1000 |  | 0
B900.6 | Plant 1 acre of woodlots | acres | 1 |  | 0
B900.7 | Uproot / cut down invasive species of trees, grass, shrub & thicket | acres | 3 |  | 0
Promote better sanitation and hygiene practices around sources
C900.1 | Support 15 households to construct lined pit latrines near production wells | HHs | 15 |  | 0
Support selected community groups in climate smart agriculture (CSA) practices
D900.1 | Support 5 farmer groups in soil and water conservation technologies e.g., contours, mulching, micro irrigation. | Groups | 5 |  | 0
D900.2 | Plant soil conservation tree species in household | HHs | 20 |  | 0
| Carried to Collection |  |  |  | 0
MUTUNDA-ESS
A900.1 | Detect and remedy soil deposition in wetlands located in the project area | sum | 1 |  | 0
A900.2 | Allow for waste management including legal disposal | sum | 1 |  | 0
A900.3 | Allow for monthly assessment of water quality, air quality and noise pollution. | months | 12 |  | 0
A900.4 | Allow for management of GBV cases as specified in ESMP | sum | 1 |  | 0
A900.5 | Allow for acquisition of permits; Waste Disposal from NEMA, Water abstraction permit from DWRM, Regulated activity in wetlands from NEMA, workplace registration permit from MOGLSD | sum | 1 |  | 0
A900.6 | Approval for campsites and Hoarding areas by Kiryandongo DLG | sum | 1 |  | 0
A900.7 | Allow for Development of Contractors ESMP | sum | 1 |  | 0
MUTUNDA-SPP
Restoration of degraded areas
B900.1 | Support 2 farmers with incentives for Farmer Managed Natural Regeneration (FMNR) around 2 water sources covering at least 2 acres. | FMNR Sites | 2 |  | 0
B900.2 | Restore indigenous trees by planting 500 tree seedlings of Omukoko (Pterygota mildbraedii) and Omutuba (Ficus nantalensis). | trees | 500 |  | 0
Reforestation of woodlands, grassland, forested areas
B900.3 | Plant 2 acres of bamboo in gullies (soil erosion sites) | acres | 2 |  | 0
B900.4 | Establish tree seedling nursery bed at Mutunda SC Hqtrs (Site already in place | Tree Nursery | 1 |  | 0
B900.5 | Distribute 1,000 fruit tree seedlings (Mangoes, Ovacado, Neem, Orange, Moringa, other multipurpose trees, medicinal or ornamental plants) | tree seedlings | 1000 |  | 0
B900.6 | Plant 2 acres of woodlots | acres | 2 |  | 0
B900.7 | Uproot / cut down invasive species of trees, grass, shrub & thicket | acres | 3 |  | 0
Promote better sanitation and hygiene practices around sources
C900.1 | Support 15 households to construct lined pit latrines near production wells | HHs | 15 |  | 0
Support selected community groups in climate smart agriculture (CSA) practices
D900.1 | Support 4 farmer groups in soil and water conservation technologies e.g., contours, mulching, micro irrigation. | Groups | 4 |  | 0
D900.2 | Plant soil conservation tree species in household | HHs | 10 |  | 0
|  |  |  | Carried to Collection | 0
METHOD-RELATED CHARGES
KIR G-1.1 | Mobilisation on site | sum | 1 |  | 0
KIR G-1.2 | Demobilise on completion of the Works | sum | 1 |  | 0
KIR G-1.3 | Supply and/or erect Contractor's site offices. | sum | 1 |  | 0
KIR G-1.4 | Maintain Contractor's site offices, including all services | months | 15 |  | 0
KIR G-1.5 | Remove Contractor's site offices on completion of the Works | sum | 1 |  | 0
In the following pages, may be entered in accordance with Section 7 of CESMM4. These must distinguish between fixed and time related charges.
Fixed charge items
KIR G-1.6 | Storage sheds and workshop | Sum | 1 |  | 0
Time-related charge items
KIR G-1.7 | Supervision | Months | 15 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page KIR G-1/1 |  |  |  | 0
| Collection, Page KIR G-1/2 |  |  |  | 0
| Collection, Page KIR G-1/3 |  |  |  | 90000000
| Collection, Page KIR G-1/4 |  |  |  | 0
| Collection, Page KIR G-1/5 |  |  |  | 0
| Collection, Page KIR G-1/6 |  |  |  | 0
|  |  |  | Carried to Summary | 90000000

## KIR G-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
KIRYANDONGO THREE RGCs PIPED WATER SUPPLY AND SANITATION SYSTEMS
BILL No. KIR G-2
DESCRIPTION: DAYWORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
DESCRIPTION
Personnel
KIR G-2.1 | Working ganger | hr | 1000
KIR G-2.2 | Artisan | hr | 2000
KIR G-2.3 | Semi-skilled | hr | 2000
KIR G-2.4 | Unskilled | hr | 2000
KIR G-2.5 | Driver for light vehicle | hr | 1500
KIR G-2.6 | Driver for heavy vehicle | hr | 1000
KIR G-2.7 | Operator for heavy equipment | hr | 500
Materials
KIR G-2.8 | Ordinary Portland Cement in 50 kg bags | t | 5
KIR G-2.9 | Coarse aggregate for concrete. | m³ | 200
KIR G-2.10 | Fine aggregate for concrete. | m³ | 500
KIR G-2.11 | Water for concrete | lit | 1500
KIR G-2.12 | Sand for building | m³ | 300
KIR G-2.13 | Sand for plaster | m³ | 300
KIR G-2.14 | Bricks for building. | nr | 4000
KIR G-2.15 | Concrete blocks for building, 225 mm for building,150 mm thick | m² | 200
KIR G-2.16 | Concrete blocks for building, 150 mm thick. | m² | 200
KIR G-2.17 | Hydrated lime for building 150 mm thick. | kg | 1000
KIR G-2.18 | Timber, sawn. | m³ | 10
KIR G-2.19 | Timber wrot. | m³ | 10
KIR G-2.20 | High yield steel reinforcement:-
KIR G-2.21 | 8-10 mm dia | kg | 500
High yield steel reinforcement:-
KIR G-2.22 | 12-16 mm dia. | kg | 400
KIR G-2.23 | Steel reinforcement fabric S reference:A252 | m² | 400
KIR G-2.24 | Hardcore filling | m³ | 600
KIR G-2.25 | Topsoil delivered to site | m³ | 400
CONTRACTOR'S EQUIPMENT
KIR G-2.26 | Road vehicles:Pick-up,1 1/2t. | hr | 100
Road vehicles: Lorries:
KIR G-2.27 | Flat-5t capacity | hr | 100
KIR G-2.28 | Flat-10t capacity | hr | 100
Tipping :
KIR G-2.29 | 5t capacity | hr | 100
KIR G-2.30 | 10t capacity | hr | 100
Water tankers with pump and hoses:
KIR G-2.31 | 5,000 lit capacity. | hr | 100
|  |  |  | Carried to Collection | 0
Excavation, face shovel or dragline:
KIR G-2.32 | 0.25 m3 bucket. | hr | 100
KIR G-2.33 | 0.5m3 bucket. | hr | 100
KIR G-2.34 | 1.0m3 bucket. | hr | 100
Tractors:
KIR G-2.35 | rubber tyred with trailer, 75 kw. | hr | 100
KIR G-2.36 | tracked including bull and angle dozer with ripper:
| (i) 150 kw. | hr | 100
| (ii) 200 kw | hr | 100
| (iii) 250 kw. | hr | 100
Rollers:
KIR G-2.37 | manual, 250 kg | hr | 100
KIR G-2.38 | vibratory, self, propelled, 1500 kg. | hr | 100
Concrete mixers with weigh batchers and loading hoppers:
KIR G-2.39 | 150 lit capacity. | hr | 100
Concrete vibrator, pneumatic with hoses:
KIR G-2.40 | poker type, 50 mm | hr | 100
Bar bending and shearing machines:
KIR G-2.41 | bending:-
| (1) hand operated. | hr | 100
KIR G-2.42 | shearing:-
| (1) hand operated | hr | 100
Air compressor, mobile with 5m of hose and steels with:
KIR G-2.43 | 1 breaker. | hr | 200
KIR G-2.44 | 2 breakers. | hr | 200
Mobile electricity generating sets, 240v, 1 ph, 50 Hz:
KIR G-2.45 | 5 kvA | hr | 200
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page KIR G-2/1 |  |  |  | 0
| Collection, Page KIR G-2/2 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## Summary-Gaspa
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
CONSTRUCTION OF GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
Grand Summary
Bill No | Description | Investment Costs
UShs
WATER SUPPLY AND EQUIPMENT
GPA W-1 | Borehole Pump Station (DWD 77381) | 0
GPA W-2 | Borehole Pump Station (DWD 77380) | 0
GPA W-3 | Borehole Pumping Mains (DWD 77380) | 0
GPA W-4 | Storage Reservoir and Site Works | 0
GPA W-5 | Distribution Network | 0
GPA W-6 | Intensification Network | 0
GPA W-7 | Chemical House (1No.) | 0
GPA W-8 | Borehole Guard / Attendant House (1No.) | 0
GPA W-9 | Water Office Block | 0
GPA ME-1 | Mechanical & Electrical Works (DWD 77381) | 0
GPA ME-2 | Mechanical & Electrical Works (Water Office) | 0
GPA ME-3 | Mechanical & Electrical Works (Chemical House - 1No.) | 0
GPA ME-4 | Tools and Equipment | 0
SANITATION
GPA S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
GPA S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
GPA S-3 | 4 Stance Waterborne Toilet - 2No. | 0
0
| Sub-Total 1 | 0
| Allow for 10% contingency | 0
| Sub-Total 2 | 0
| Allow for 18% VAT | 0
| GRAND TOTAL | 0

## GPA W-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-1
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77381
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
15000
D310 | Diameter 150-500 mm | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 708 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 212 |  | 0
MISCELLANEOUS WORKS
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-1/1 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA W-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-2
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77380
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance including clearance of access road to the site | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
15000
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 49 |  | 0
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 33.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to pump house area and compacted to 98% MOD AASHTO | m³ | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.9 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 7.9 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 213 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.9 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and generator plinth of the following thickness
F622 | Thickness 150-300mm | m³ | 38 |  | 0
Suspended Slabs
Placing reinforced concrete, grade C25, for false slab (ceiling) of the following thickness
F631 | Thickness not exceeding 150mm | m³ | 1.9 |  | 0
|  |  |  | Carried to Collection | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to floor and pump house of the following width
G214 | Width: 0.4-1.22m; to false slab soffits | m² | 38.6 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244.1 | Width: 0.4-1.22m; to floor and generator plinth | m² | 5.7 |  | 0
G244.2 | Width: 0.4-1.22m; to sides of the ring beam | m² | 4.5 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 156 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 26.5 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of Pump Stations | m2 | 40.6 |  | 0
PIPEWORK - FITTINGS AND VALVES
Pipework and Fittings for DWD 77380 with yield of 37.0m3/hr
Ductile spun iron/ steel pipes with spigot and socket type joints and cement mortar linings, 100 mm ND DI PN16 Pipes, all to EN 545 and including approved rubber gaskets, trench excavation, lowering, laying and jointing of pipes; not in trenches including casting in as required
All pipe specials are annotated and specified on the pump station drawing. The code indicated refers to the code on the drawing.
Bends
J311.1 | BH11 - DN 100mm x 45deg flanged small radius bend | No | 2 |  | 0
J311.2 | BH23 - DN 100mm x 90deg flanged small radius bend | No | 2 |  | 0
|  |  |  | Carried to Collection | 0
Junctions and Branches
J312.1 | BH6 - DN 100mm flanged tee with 25mm female threaded branch | No | 2 |  | 0
Adaptors
J351.1 | BH8 - DN 15mm diam. Hexagon nipple | No | 1 |  | 0
J351.2 | BH16 - DN 25mm diam. Hexagon nipple | No | 2 |  | 0
J351.3 | BH2 - DN100mm Detachable / Maxi Flanged coupling | No | 2 |  | 0
Glands
J361.1 | BH4 - DN 100mm Double-flexible rubber pipe flanged coupling | No | 2 |  | 0
Straight specials - DN 100 mm pipe with fittings
J381.1 | BH1 - plain threaded both ends, nominally 3000mm long, cut to suit on site | No | 1 |  | 0
J381.2 | BH3 - DN100 Steel/DI/HDPE/uPVC PN16 riser pipes from submersible pump to top plate; complete to match pump outlet size and pumphouse pipe work | m | 100 |  | 0
J381.3 | BH12 - flanged both ends, 800mm f/f | No | 1 |  | 0
J381.4 | BH14 - flanged both ends, 400mm f/f | No | 1 |  | 0
J381.5 | BH19 - flanged both end, nominally 1500mm, cut-to-suit on site | No | 1 |  | 0
Gate Valves
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | DN 100mm | No | 2 |  | 0
Air Valves
BH 18- Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 50 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J861.1 | DN 100mm | No | 1 |  | 0
|  |  |  | Carried to Collection | 0
Pressure Gauge
J891.1 | BH10 - WIKA pressure gauge, DN 100mm case, glycerine filled with 15mm male thread | No | 1 |  | 0
Non-Return Valves
BH 15 - Flanged Non return Valves shall confirming to BS EN 12334:2001, flanges to EN 1092, all to PN16 the follwing pipe sizes.
J861.1 | DN 100mm | No | 1 |  | 0
Bulk Flow Meter
J991.1 | BH13 - flanged DN 100mm MEINECKE Cosmos WP bulk water meter | No | 1 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Isolated pipe supports
L811 | Pipe support 1 - mass concrete 200mm x 200mm x 600mm high, Class 20/20, complete with shuttering, to pipes | nr | 1 |  | 0
L812 | Pipe support 2 - mass concrete 200mm x 200mm x nominal 500mm high, Class 20/20, complete with shuttering, to valve (BH15) and tee (BH6) | nr | 2 |  | 0
L813 | Pipe support 3 - mass concrete 500mm x300mm x nominal 500mm high, Class 20/20, complete with shuttering, to bend | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 654 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 197 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 10 |  | 0
PAVINGS
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 36 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces, as detailed in the drawings, for walls of the following thickness
U521 | 230 mm thick | m2 | 99.2 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.9 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 34.6 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 61.2 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 26.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 25.7 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 38.6 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 50.6 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 48.4 |  | 0
MISCELLANEOUS WORKS
Roofing
GPA W-2.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board and all roofing timber, eave closing, gauge 26 prepainted GCI resin sheeting and ridges | m² | 38.7 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories, including aluminium mosquito proof wire gauze welded to mild steel frames in 300mm high permanent vents
GPA W-2.2 | Single leaf steel door, size 900 x 2400mm with 700mm high 4mm thick glass panes and burglar proofing; complete | nr | 1 |  | 0
GPA W-2.3 | Double leaf door overall size 1800 x 2400mm high filled in with 20 x 2mm thick mild steel square hollow section grating welded to door, complete | nr | 1 |  | 0
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
GPA W-2.4 | Steel frame glazed window, 1200mm by 2000mm clear opening; include frame, glazing, all iron mongery | nr | 3 |  | 0
Building Finishes
GPA W-2.5 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-2/1 |  |  |  | 0
| Collection, Page GPA W-2/2 |  |  |  | 0
| Collection, Page GPA W-2/3 |  |  |  | 0
| Collection, Page GPA W-2/4 |  |  |  | 0
| Collection, Page GPA W-2/5 |  |  |  | 0
| Collection, Page GPA W-2/6 |  |  |  | 0
| Collection, Page GPA W-2/7 |  |  |  | 0
| Collection, Page GPA W-2/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA W-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-3
DESCRIPTION: BOREHOLE PUMPING MAINS DWD 77380
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 7940 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 5 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 3 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS EN1452, with flexible joints to BS EN14814 all to PN10, OD160mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 6617 |  | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Flanged adaptor to fit uPVC pipe spigots to BS 3505, flanges to BS 4505, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 12 |  | 0
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.1 | 150 mm ND | nr | 4 |  | 0
Ductile Iron all flanged 45 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.2 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 22.5 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.3 | 150 mm ND | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 25 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN10 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 150 mm ND | nr | 1 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valves, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes;all to PN10
J911.1 | 150 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 1 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 1 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.1 | Diameter not exceeding 300 mm ND | m | 12 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes | nr | 17 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 148.8825 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 6 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 100 mm ND | m | 5367 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 100 mm ND | m | 1000 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 100 mm ND | m | 250 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-3/1 |  |  |  | 0
| Collection, Page GPA W-3/2 |  |  |  | 0
| Collection, Page GPA W-3/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA W-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-4
DESCRIPTION: STORAGE RESERVOIR AND SITE WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for works | m2 | 625 |  | 0
EARTHWORKS
General Excavation
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 7.4 |  | 0
Excavation for foundations
Ordinary Soil
Excavation for foundations (stub columns), in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth 0.5-1m | m³ | 20.3 |  | 0
E324 | Depth 1-2m | m³ | 10.1 |  | 0
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5 - 1.0 m | m³ | 1 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces in the following materials
E522 | Material other than topsoil, rock or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 54 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 27 |  | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 9.8 |  | 0
E533 | Rock | m³ | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 10.4 |  | 0
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to foundations and compacted to 98% MOD AASHTO | m³ | 1 |  | 0
Filling Ancillaries
Trimming of Filled Surfaces
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 54 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 27 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 425 |  | 0
Provision of Hardcore
E810 | Provision and placement of 300mm thick hardcore base for the tank footings | m² | 20.3 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F131 | 10 mm aggregate | m³ | 1 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F151 | 10 mm aggregate | m³ | 9.8 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, grade C15, of the following thickness
F512 | Thickness 150-300mm | m³ | 1 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete, grade C25, for column base footings of the following thickness
F522 | Thickness 300-500 mm | m³ | 8.1 |  | 0
Columns
Placing reinforced concrete, grade C25, for columns of the following thickness
F522 | Thickness 300-500 mm | m³ | 1.7 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G245 | Width exceeding 1.22m | m² | 38.9 |  | 0
Reinforcement
High Yield Steel
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 1225 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G812 | With steel float finish | m² | 17.3 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK - PIPES
Plastic Drain Pipes
uPVC drain pipes, conforming to BS EN1452, ith flexible joints to BS EN14814, 225 mm OD PN 6, laid in trench to the following depths
I512 | Depth not exceeding 1.5m | m | 30 |  | 0
PIPEWORK - FITTINGS AND VALVES
Cast or Spun Iron Pipe Fittings
external epoxy coated to AWWA C213
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.1 | 100 mm ND | nr | 1 |  | 0
J311.2 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.3 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.4 | 150 mm ND | nr | 2 |  | 0
J311.5 | 200 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.6 | 150 mm ND | nr | 1 |  | 0
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 200/100 mm ND | nr | 1 |  | 0
Double Collars
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J341.1 | 150 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 16, and of the following sizes
J341.2 | 150 mm ND | nr | 1 |  | 0
Adaptors
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 200 mm ND | nr | 1 |  | 0
J351.2 | 150 mm ND | nr | 2 |  | 0
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN16, and of the following sizes
J351.3 | 150 mm ND | nr | 1 |  | 0
Bellmouths
Flanged bellmouth to ISO 2531, flanges to ISO 2441, of the following sizes all to PN 10
J372.1 | 200 mm ND | nr | 1 |  | 0
Straight Specials
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 10 and of the following sizes
J381.1 | 100 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.2 | 100 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.3 | 150 mm ND not exceeding 0.6m | nr | 4 |  | 0
J381.4 | 150 mm ND not exceeding 1.0m | nr | 2 |  | 0
J381.5 | 150 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.6 | 150 mm ND not exceeding 6.0m | nr | 4 |  | 0
J381.7 | 200 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.8 | 200 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.9 | 200 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.10 | 200 mm ND not exceeding 6.0m | nr | 2 |  | 0
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 16 and of the following sizes
J381.11 | 150 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.12 | 150 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.13 | 150 mm ND not exceeding 3.0m | nr | 1 |  | 0
J381.14 | 150 mm ND not exceeding 6.0m | nr | 2 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491.1 | 150 mm ND | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 100 mm ND | nr | 1 |  | 0
J811.2 | 150 mm ND | nr | 1 |  | 0
Ball Float Valves
Flanged Balanced ball float valve, flanges to BS 4505, all to PN16
J891.1 | 150 mm ND | nr | 1 |  | 0
Bulk Flow Meter
"Woltman" Helix Type Bulk Flow Meter inclusive of all couplings, adaptors, steel pipe distance pieces, CI valves, thrust blocks, etc and all other fittings to make the installation complete, as specified, all fittings to PN 10, including lockable vented blockwork chamber with cast in valve surface boxes, and on the following main pipe sizes
J991.1 | 150 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Manholes
Blockwork Manhole
Blockwork chamber complete with C20 concrete base, vented lockable manhole cover, valve surface boxes, galvanised step irons, as specified in the drawings, and of the following depths
K171 | Depth not exceeding 1.5m | nr | 2 |  | 0
Other Chambers
In situ Concrete Chambers
Washout out fall structure, complete including flap valve, all fittings and pipework necessary to complete installation, as specified in drawings, and of the following depths; all fittings and pipework to PN 10
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Supply and construct grouted stone pitching using mortar mix 1:4, include 50mm thick coping using 1:2:4 concrete mix on top of the stone pitching of same width as the wall thickness for drains of cross section
K 491 | Cross section area 0.5-1.0m2 | m | 20 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 1 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for bulk meters | nr | 1 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 300 mm ND | m | 20 |  | 0
MISCELLANEOUS WORKS
Supply and Install cold pressed galvanised steel sectional tank with external flanges and pitched cover with 1No. 1m wide access man way, 15m high tower, water level indicator (scale in cubic metres) and plates with inlet, outlet, washout and overflow connection complete with access points, ventilators (4 nr), walkway, handrailing, and internal and external access ladders with safety hoops, inclusive of painting, finishes and all necessary accessories to installation complete as specified and detailed in the drawings; to the Engineer's satisfaction. All tank accessories shall be of hot dipped galvanised steel.
GPA W-4.1 | Reservoir: 200m3 nominal capacity erected on a 15m high tower | nr | 1 |  | 0
GPA W-4.2 | Supply and Installation of a 15m high steel tower | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 60 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 18 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-4/1 |  |  |  | 0
| Collection, Page GPA W-4/2 |  |  |  | 0
| Collection, Page GPA W-4/3 |  |  |  | 0
| Collection, Page GPA W-4/4 |  |  |  | 0
| Collection, Page GPA W-4/5 |  |  |  | 0
| Collection, Page GPA W-4/6 |  |  |  | 0
| Collection, Page GPA W-4/7 |  |  |  | 0
| Collection, Page GPA W-4/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA W-5
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-5
DESCRIPTION: DISTRIBUTION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 21504 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 5 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 4 |  | 0
D320 | Diameter 500 mm -1 m | nr | 4 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to all to PN10, OD160mm, laid in trench to the following depths
I512.1 | Depth not exceeding 1.5m | m | 2935 |  | 0
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to BS4346 all to PN10, OD110mm, laid in trench to the following depths
I512.2 | Depth not exceeding 1.5m | m | 24 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 90mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 5141 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 63mm, laid in trench to the following depths
I712.2 | Depth not exceeding 1.5m | m | 7724 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 50mm, laid in trench to the following depths
I712.3 | Depth not exceeding 1.5m | m | 2096 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 150/150 mm ND | nr | 1 |  | 0
J321.2 | 150/80 mm ND | nr | 1 |  | 0
J321.3 | 100/80 mm ND | nr | 1 |  | 0
J321.4 | 50/40 mm ND | nr | 1 |  | 0
Tapers
Ductile iron all flanged concentric taper to EN 545, flanges to EN 1092-2 all to PN10, cement mortar lined, and of the following sizes
J331.1 | 150/80 mm ND | nr | 1 |  | 0
J331.2 | 100/80 mm ND | nr | 1 |  | 0
J331.3 | 100/50 mm ND | nr | 1 |  | 0
J331.4 | 80/40 mm ND | nr | 1 |  | 0
J331.5 | 50/40 mm ND | nr | 2 |  | 0
Adaptors
Flanged adaptor to fit uPVC pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 3 |  | 0
J351.2 | 100 mm ND | nr | 2 |  | 0
Plastic Pipe Fittings
Bends
uPVC 90 degree bends with push-fit joint for use with uPVC pipes, to EN 1401, all to PN 10, and of the following sizes
J311.1 | 150mm ND | nr | 2 |  | 0
uPVC 22.5 degree bends with push-fit joint for use with uPVC pipes, to EN 1401, all to PN 10, and of the following sizes
J311.2 | 150mm ND | nr | 1 |  | 0
HDPE 90 degree bends for use with HDPE pipes, to EN12201, all to PN 10, and of the following sizes
J311.3 | 50mm ND | nr | 1 |  | 0
Adaptors
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.1 | OD 90 mm X 3" | nr | 2 |  | 0
J651.2 | OD 63 mm X 2" | nr | 6 |  | 0
J651.3 | OD 50 mm X 1 1/2" | nr | 3 |  | 0
|  |  |  | Carried to Collection | 0
End caps
Compression HDPE end caps to fit uPVC spigots, to EN 12201 and to PN 10 of the following spigot sizes
J691.1 | ND 50 mm | nr | 2 |  | 0
J691.2 | ND 40 mm | nr | 3 |  | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 2 |  | 0
J811.2 | 100 mm ND | nr | 2 |  | 0
J811.3 | 50 mm ND | nr | 4 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 25 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN10, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 80 mm ND | nr | 1 |  | 0
J862.2 | 50 mm ND | nr | 1 |  | 0
Washouts
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 80 mm ND | nr | 2 |  | 0
J911.2 | 50 mm ND | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 4 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 2 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 8 |  | 0
|  |  |  | Carried to Collection | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 6 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 48 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 8 |  | 0
K820.2 | Marker posts for air valves | nr | 2 |  | 0
K820.3 | Marker posts for wash outs | nr | 4 |  | 0
K820.4 | Marker posts for pipes | nr | 45 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 403.2 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 11 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 15920 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-5/1 |  |  |  | 0
| Collection, Page GPA W-5/2 |  |  |  | 0
| Collection, Page GPA W-5/3 |  |  |  | 0
| Collection, Page GPA W-5/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA W-6
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-6
DESCRIPTION: INTENSIFICATION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | m2 | 14400 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
PIPEWORK-PIPES
Plastic Pressure Pipes- Distribution
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 40 mm, laid in trench to the following depths
I711.1 | Depth not exceeding 1.5m | m | 2000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 32 mm, laid in trench to the following depths
I711.2 | Depth not exceeding 1.5m | m | 2000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 25 mm, laid in trench to the following depths
I711.3 | Depth not exceeding 1.5m | m | 2000 |  | 0
12
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD32 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 2 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
Make a connection for OD25 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 2 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 8 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
K731 | Not exceeding 300 mm ND | m | 56 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 135 |  | 0
|  |  |  | Carried to Collection | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 4000 |  | 0
Pipe surrounds, of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds, of mass concrete , for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
Consumer Connections
Make DN20 consumer connection to the distribution main (maximum 100m), complete, inclusive of excavation, backfill, saddle clamp, ferrule, taps,domestic water meter and all fittings for connection to GI or HDPE service pipes, as detailed in the drawings, for the following mains sizes and all to PN10
J891.1 | ND 40 mm | nr | 80 |  | 0
J891.2 | ND 50 mm | nr | 40 |  | 0
J891.3 | ND 65 mm | nr | 40 |  | 0
J891.4 | ND 100 mm | nr | 40 |  | 0
J891.5 | ND 150 mm | nr | 40 |  | 0
Public Stand Posts
Construct a double faucet Stand Post complete as in drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fitings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN 10 (service line measured separately under items I712)
L999.1 | ND 20 mm (3/4") | nr | 15 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-6/1 |  |  |  | 0
| Collection, Page GPA W-6/2 |  |  |  | 0
| Collection, Page GPA W-6/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## GPA W-7
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-7
DESCRIPTION: CHEMICAL HOUSE (1No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5 - 1.0 m | m³ | 26.7 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 0.8 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 25.4 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 2.4 |  | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 15.6 |  | 0
E533 | Rock | m³ | 0.8 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling Ancillaries
Filling
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated granular material other than topsoil, rock or artificial hard material compacted to 98% MOD AASHTO | m³ | 11.1 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.1 |  | 0
|  |  |  | Carried to Collection | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 6.3 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 40.1 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 3.8 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.3 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 4.35 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.3 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C25, for floor slab, stairs and tank base of the following thickness
F622 | Thickness 150-300mm | m³ | 3.3 |  | 0
Beams
Placing reinforced concrete grade C25, for ring beam of the following cross-sectional area
F562 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.05 |  | 0
|  |  |  | Carried to Collection | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G212 | Width: 0.1-0.2m | m² | 5.1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G243 | Width: 0.2-0.4m | m² | 20 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS 4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 304 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 22.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 22.5 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U523 | 200 mm thick | m² | 90 |  | 0
Permanent Vents
Construct dense concrete pre-cast louvered blockwork vents to BS 7263, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U590.1 | 1500mm x 1200mm (W x H) | nr | 1 |  | 0
U590.2 | 2600mm x 1200mm (W x H) | nr | 3 |  | 0
|  |  |  | Carried to Collection | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.7 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 12.6 |  | 0
Emulsion Paint
Masonry
Internal quality emulsion paint, two coats, to the following smooth masonry surfaces, include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 71 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 22.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 22.2 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 20.7 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 44 |  | 0
|  |  |  | Carried to Collection | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 44 |  | 0
MISCELLANEOUS WORKS
Doors
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA W-7.1 | 900mm x 2400mm (W x H including 300mm wood pvo) | nr | 2 |  | 0
Roofing
GPA W-7.2 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI resin sheeting and ridges; the GCI sheet should be resin bonded or with other protection against corrosion by Chlorine | m² | 35 |  | 0
GPA W-7.3 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 20.7 |  | 0
Building Finishes
GPA W-7.4 | Chemical house finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 600mm wide C20 concrete splash apron, 2 no. drainage manholes of internal dimension 700x700mm with OD 110 PVC drainage pipework to soak pit included, 300mm x 1380mm x 100mm thick reinforced concrete doser plinth cover slabs over inlet pipe channel, etc complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
GPA W-7.5 | Supply, lay and fix inlet pipes, valves and fittings; including ball valves and flowmeter; from the outlet pipe of the nearby reservoir tank to the water tank of size OD32mm, all pipe and fittings in HDPE/uPVC/PPR to PN 10 as approved by the Engineer | Sum | 1 |  | 0
GPA W-7.6 | Supply, lay and fix drain pipes, valves and fittings from the tanks to the nearest manhole, as in the drawings, of size OD63mm, all pipe and fittings in HDPE/uPVC/PPR to PN10 as approved by the Engineer; include manhole connection and making good joint | Sum | 1 |  | 0
Mixing Tanks
GPA W-7.7 | Supply and install chlorine generation and dosing PVC tanks of 750 litres capacity as specified and as approved by the Engineer; include complete connection to Electrolytic Disinfecting Machine, Dosing equipment, and incoming DN150mm uPVC pumping Main | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-7/1 |  |  |  | 0
| Collection, Page GPA W-7/2 |  |  |  | 0
| Collection, Page GPA W-7/3 |  |  |  | 0
| Collection, Page GPA W-7/4 |  |  |  | 0
| Collection, Page GPA W-7/5 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## GPA W-8
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-8
DESCRIPTION: GUARD AND PUMP ATTENDANT HOUSE (1No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 38.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to building area and compacted to 98% MOD AASHTO | m³ | 5.45 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 0.79 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 4.75 |  | 0
|  |  |  | Carried to Collection | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.25 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.36 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 2.25 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and steps of the following thickness
F622 | Thickness 150-300mm | m³ | 2.85 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.51 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width: 0.4-1.22m | m² | 1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width: 0.4-1.22m; to sides of the ring beam | m² | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 186 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 16 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 16 |  | 0
BRICKWORK, BLOCKWORK, AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U521.1 | 150 mm thick | m2 | 42.2 |  | 0
U521.2 | 230 mm thick | m² | 33.1 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.4 |  | 0
Masonry
External quality weather guard paint two coats, to the following smooth concrete surfaces; include surface preparation as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 4.5 |  | 0
|  |  |  | Carried to Collection | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 46 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 21 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.2 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 39.3 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 53.7 |  | 0
MISCELLANEOUS WORKS
Roofing
GPA W-8.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes to the Engineer's satisfaction. | m2 | 15 |  | 0
GPA W-8.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600x600mm hardwood access trap door | m² | 14 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
GPA W-8.3 | Mild steel window overall size 1000 x 1100mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
GPA W-8.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
GPA W-8.5 | Single leaf solid steel door, size 900 x 2100mm; complete | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA W-8.6 | 800mm x 2100mm (W x H) | nr | 2 |  | 0
Building Finishes
GPA W-8.7 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
GPA W-8.8 | Supply and install a 1500 litre (1.5m3) Polyethylene tank as Polytank, elevated up to 1.0m above ground level on a rendered brickwork platform, complete with a DN 15mm Brass outlet tap, inlet DN 80 uPVC pipe work from overhead rain water gutters, DN 80 uPVC overflow and drainage pipework to soak pit (inclusive) as per drawings | Sum | 1 |  | 0
GPA W-8.9 | Provide and fix urine diverting squat pans as directed by Engineer | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Plumbing and Drainage
GPA W-8.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
GPA W-8.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
GPA W-8.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
GPA W-8.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
GPA W-8.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
GPA W-8.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-8/1 |  |  |  | 0
| Collection, Page GPA W-8/2 |  |  |  | 0
| Collection, Page GPA W-8/3 |  |  |  | 0
| Collection, Page GPA W-8/4 |  |  |  | 0
| Collection, Page GPA W-8/5 |  |  |  | 0
| Collection, Page GPA W-8/6 |  |  |  | 0
| Cost for 1No. Attendant House |  |  |  | 0
| Total Cost of Attendant Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## GPA W-9
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA W-9
DESCRIPTION: WATER OFFICE BLOCK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for office premises | ha | 0.1 |  | 0
Trees
Cut and dispose of trees of the following girths; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5-1m | m³ | 52 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 1 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
|  |  | 67 |  | 0
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
|  |  | 1.5 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 18 |  | 0
E533 | Rock | m³ | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to office area and compacted to 98% MOD AASHTO | m³ | 26 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.7 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 10 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 24 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 4 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 600 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.2 |  | 0
0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 21 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.2 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab of the following thickness
F622 | Thickness 150-300mm | m³ | 17.9 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 3 |  | 0
Columns and Piers
Placing reinforced concrete, grade C25, for columns of the following cross-sectional area
F652 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.12 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to office block of the following width
G213 | Width 0.2 - 0.4m | m² | 7 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G241 | Width not exceeding 0.15m | m² | 6 |  | 0
G243 | Width 0.2 - 0.4m | m² | 33 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 577 |  | 0
0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 98 |  | 0
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of office block | m2 | 98 |  | 0
ROADS AND PAVINGS
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO lime stabilised gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 200 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 30 |  | 0
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 48 |  | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U211 | 100 mm thick; Facing Bricks | m2 | 60 |  | 0
U521.1 | 150 mm thick | m2 | 12 |  | 0
U521.2 | 230 mm thick | m2 | 164 |  | 0
Permanent Vents
Dense brickwork vents to BS 7263, jointed with ordinary 1:5 cement mortar above door and window openings, including mosquito mesh, for walls of the following thickness
U589 | 150 - 230 mm thick | m2 | 3 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 8 |  | 0
0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 40 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 192 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 60.7 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified.
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
MISCELLANEOUS WORKS
Roofing
GPA W-9.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes connected to 3000m3 rain water polytank placed on 1m high masonry platform & complete with the necessary piping to the Engineer's satisfaction. | m2 | 136.8 |  | 0
GPA W-9.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 136.8 |  | 0
0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
GPA W-9.3 | Mild steel window overall size 1500 x 1200mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 4 |  | 0
GPA W-9.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick glass panes, and burglar proofing | nr | 2 |  | 0
GPA W-9.5 | Mild steel top hang window overall size 600 x 450mm with 2 No. 300 x 300 mm clear opening and fixed sashes complete | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
GPA W-9.6 | Double leaf steel casement door overall size 1200 x 2100mm high complete with 4mm thick clear glass panes and burglar proofing | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA W-9.7 | 900mm x 2100mm (W x H) | nr | 3 |  | 0
Fences
GPA W-9.8 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
GPA W-9.9 | Width 4 m, double leaf complete | nr | 1 |  | 0
Building Finishes
GPA W-9.10 | Building finishes including; constructing C20 1.0x2.0m entrance ramp, 20x100mm high ceramic skirting, 1500mm high toilet walls and floor ceramic tiling, C20 concrete window cills, 700mm wide C20 concrete splash apron; Soft board notice board fixed to the wall, area 1.5 m2, complete to the specifications and as directed by the Engineer | Sum | 1 |  | 0
GPA W-9.11 | Construct in hardwood timber 3.25m x 0.7m x 0.7m high storage shelves on 4mm thick steel angle frames, 3 levels; installed in the main store, as directed by the Engineer | sum | 1 |  | 0
0
Plumbing and Drainage
GPA W-9.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
GPA W-9.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
GPA W-9.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
GPA W-9.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
GPA W-9.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
GPA W-9.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA W-9/1 |  |  |  | 0
| Collection, Page GPA W-9/2 |  |  |  | 0
| Collection, Page GPA W-9/3 |  |  |  | 0
| Collection, Page GPA W-9/4 |  |  |  | 0
| Collection, Page GPA W-9/5 |  |  |  | 0
| Collection, Page GPA W-9/6 |  |  |  | 0
| Collection, Page GPA W-9/7 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA ME-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA ME-1
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS DWD 77380
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Borehole Pumps
ME 1.1.1 | Electric multistage centrifigual submersible borehole pumpset with motor, capacity Q = 30.0m3/hr at a head of 116m delivering to Reservoir; complete with starter, delivery pressure gauge, pressure switch, protective controls against dry runs, and all accessories as Grundfos or equal approved | No. | 1 |  | 0
0
ME 1.1.2 | Manufacturer's recommended spares for 3 years operation of 1No. borehole pumps including 1no. spare motor for the pump | Set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Borehole Pump, Guard and Attendant Houses
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 4 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 4 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 3 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 6 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 6 |  | 0
EE 1.2 | Earthing and Lightning Protection
EE 1.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 12 |  | 0
EE 1.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 3 |  | 0
EE 1.2.3 | Test clamp complete as by FURSE or equal. | No. | 3 |  | 0
EE 1.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 3 |  | 0
EE 1.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | M | 20 |  | 0
EE 1.2.6 | 100KVA Electronic stabilizer rated at 400V, 50Hz 3 phase, input voltage +/-25%, output voltage +/-5%, complete with independent phase control, input/output isolators and bypass switch and all accessories as made by Orteo of Italy or equal approved. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 1.2.7 | Motor Control Centre for borehole incorporating main circuit breaker, starter, controls and protection for pump (HIGH/LOW pressure and dry running), under and overvoltage relay and single phasing relay, power monitor, hour, volt and Amp meters, and all accessories complete as in specifications | No. | 1 |  | 0
EE 1.2.8 | Armoured cable 4corex10mm2 PVC/SWA/PVC laid in conduits to pumps complete | m | 85 |  | 0
Power Supply to Pump House
EE 1.3 | Solar Power
EE 1.3.1 | Supply and Installation of additional mono crystalline PV Solar panels rated at 280pW 12 Volts DC, include: PV solar panel support structure for mounting solar panels; all electrical accessories; to the Engineer's approval | No. | 162 |  | 0
EE 1.4 | Standby Generator
EE 1.4.1 | Supply and install a three phase electrical diesel driven generator set of Prime power 100kVA; complete with heavy duty steel skid type base plate frame with anti vibration mounting pads; electrical starter including a heavy duty lead acid battery, and charging system: exhaust silencer with connections: automatic engine shut down with LED indicators: mounted control panel including suitably rated MCCB: Suitably sized fuel tank of at least 8 hour capacity: change over switch 63 Amps MEM: sound attenuated canopy. | No. | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA ME-1/1 |  |  |  | 0
| Collection, Page GPA ME-1/2 |  |  |  | 0
| Collection, Page GPA ME-1/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA ME-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA ME-2
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (WATER OFFICE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Water Office
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 8 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 10 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 2 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 8 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 8 |  | 0
EE 2.1 | Earthing and Lightning Protection
EE 2.1.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 30 |  | 0
EE 2.1.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 4 |  | 0
EE 2.1.3 | Test clamp complete as by FURSE or equal. | No. | 4 |  | 0
EE 2.1.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 4 |  | 0
EE 2.1.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.1.6 | 63A TPN IP65 Isolator. | No. | 2 |  | 0
EE 2.1.6 | 100A TPN IP65 Isolator. | No. | 2 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 2.2 | Power Supply to Water Office |  |  | 0
0
EE 2.2.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA ME-2/1 |  |  |  | 0
| Collection, Page GPA ME-2/2 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA ME-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA ME-3
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (CHEMICAL HOUSE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Chlorine Generation & Dosing Equipment |  |  | 0
0
ME 1.1.1 | Supply and Install DOSATRON D60S model or equivalent in line proportional chemical doser or its equivalent approved by the Engineer including all inlet, outlet, drain, venturi, overflow and interconnection connection pipes to solution tank (PVC, 1") with valves and all accessories with a minimum capacity of 10-60m3/hr | nr | 1 |  | 0
ME 1.1.2 | Manual geared vertical mixers- agitators- propeller 2 blade type, stainless steel shaft, coupling, propeller diameter 600mm, fixed to rigid steel structure complete. | nr | 1 |  | 0
ME 1.1.3 | Rigid steel structure - made of black mild steel double L- profiles; intermediate stands - hot dip galvanized & coated, complete with base plates, anchors, nuts, bolts & washers, etc | nr | 1 |  | 0
ME 1.1.4 | Manufacturer's recommended spares for 3 years operation of dosing pumps | set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Chemical House
EE 2.1 | Lighting and Small Power
EE 2.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 2 |  | 0
EE 2.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 2 |  | 0
EE 2.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 1 |  | 0
EE 2.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 1 |  | 0
EE 2.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 1 |  | 0
EE 2.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 1 |  | 0
EE 2.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 1 |  | 0
EE 2.2 | Earthing and Lightning Protection
EE 2.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 20 |  | 0
EE 2.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 1 |  | 0
EE 2.2.3 | Test clamp complete as by FURSE or equal. | No. | 1 |  | 0
EE 2.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 1 |  | 0
EE 2.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.2.6 | 63A TPN IP65 Isolator. | No. | 1 |  | 0
EE 2.2.6 | 100A TPN IP65 Isolator. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 2.3 | Power Supply to Chemical House |  |  | 0
0
EE 2.3.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA ME-3/1 |  |  |  | 0
| Collection, Page GPA ME-3/2 |  |  |  | 0
| Collection, Page GPA ME-3/3 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## GPA ME-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA ME-4
DESCRIPTION: TOOLS AND EQUIPMENT
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Supply of all Office, Plumbing, Mechanical, Electrical, Miscellaneous, Equipment, as detailed in SPECIFICATIONS and summarized below. Supplied Items should be to the Engineer's approval
OFFICE EQUIPMENT
OE 1.1 | Writing desk 1,560 x 780 x 750 mm (L x W x H) with closed front view and 6 lockable drawers | No. | 4 |  | 0
OE 1.2 | Executive swivel, high back tilting steel office chair with arm rests and padded seat and back in black rexine | No. | 1 |  | 0
OE 1.3 | Executive steel office chairs with padded seat and back in black rexine | No. | 3 |  | 0
OE 1.4 | Steel cabinet 1,950 x 950 x 420 mm (L x W x H) with double lockable doors, 4 shelves; colour: grey | No. | 1 |  | 0
OE 1.5 | Lockable steel filing cabinet with 4 drawers | No. | 1 |  | 0
OE 1.6 | Computer Workstation complete as specified | No. | 2 |  | 0
Intel Core i7-2500 3.30GHz, 6M Smart Cache processor
16 GB of DDR 1066 MHz SDRAM; 1TB SATA Hard Disk Drive
16X DVD +/- RW; 17” TFT “Ultra Sharp Flat Panel
Licensed Microsoft Windows 7
Licensed MS Office 2010 & Kaspersky Internet Security 2013
UPS of minimum specification 1500 VA
OE 1.7 | HP Laser Jet Printer | No. | 1 |  | 0
Printer speed- up to 24 ppm black; Processor speed- 533 MHz
Paper trays- 2 trays; Input capacity- Up to 500sheets
Memory- 544MB (512MB DDR SDRAM)
Media size- Max. A4; 10/100 Network Interface Card
5no. Replacement Toner Cartridges
Bi-directional parallel cable; USB printer cable
PLUMBING TOOLS AND EQUIPMENT
PE 2.1 | Blowlamp: pump action, pressure type, approx. 0.5 litre capacity, complete with wind proof nozzle and one set of replacement parts | No. | 2 |  | 0
PE 2.2 | Brushes, wire type for cleaning parts, 300 mm long, 3 rows of approximately15 tufts with 25 mm long steel bristles | No. | 2 |  | 0
PE 2.3 | File, flat machinist's, length 250 mm, second cut | No. | 1 |  | 0
PE 2.4 | File, flat machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.5 | File, flat machinist's, length 250 mm, bastard cut | No. | 1 |  | 0
PE 2.6 | File, half-round machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.7 | File, half-round machinist's, length 250 mm, but bastard cut | No. | 1 |  | 0
PE 2.8 | File handles, 100 x 27 mm | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
PE 2.9 | Hammer, mechanic's, 200 & tempered forged steel head, ash or white hickory handle, polished face | No. | 1 |  | 0
PE 2.10 | Precision Level, plumb and spirit, approximately 600 x 25 x 75 mm, varnished beech wood or aluminium, class of accuracy 0.025 mm/m | No. | 1 |  | 0
PE 2.11 | Mattocks | No. | 1 |  | 0
PE 2.12 | Pliers, arc joint, minimum 5 adjustments, 240 mm long | No. | 1 |  | 0
PE 2.13 | Saw, Plumbers, 400 mm, fine tooth edge for cutting metal and coarse teeth for cutting wood, complete with 5No. blades | No. | 1 |  | 0
PE 2.14 | Screw drivers, assorted, hammer-proof, non-inflammable plastic handle | Set | 1 |  | 0
PE 2.15 | Shovels | No. | 1 |  | 0
PE 2.16 | Tape measure, Stanley type steel, metric units, 5 m | No. | 1 |  | 0
PE 2.17 | Tapping machine, furnished with ratchet crank for manual operation, for making tappings from DN 15 (1/2") to DN 50 (2") on mains of DN 25 (1”) to DN 300 (12”) | No. | 1 |  | 0
PE 2.18 | Die set with stock, for threading from DN 15 to DN 150 | No. | 1 |  | 0
PE 2.19 | Vice with parallel jaw 100 mm as Peddinghaus, Matador 10203, portable type, with tripod stand | No. | 1 |  | 0
MECHANICAL TOOLS AND EQUIPMENT
ME 3.1 | 0.5 kg axe. | No. | 1 |  | 0
ME 3.2 | Caliper, precision slide type, metric unit. | No. | 1 |  | 0
ME 3.3 | Carpenter chisel from 6.4 mm to 25.4 mm bevelled edge. | Set | 1 |  | 0
ME 3.4 | Mason chisel from 25.4 mm to 50 mm wide blade. | Set | 1 |  | 0
ME 3.5 | Carpenter's screw clamps, 250 mm opening. | No. | 2 |  | 0
ME 3.6 | Carpenter's screw clamps, 500 mm opening. | No. | 2 |  | 0
ME 3.7 | Square set, metric unit. | No. | 1 |  | 0
ME 3.8 | Crowbars, small, medium, large. | Set | 1 |  | 0
ME 3.9 | Gasket cutter, 600 mm. | No. | 1 |  | 0
ME 3.10 | Dividers. | Set | 1 |  | 0
ME 3.11 | Six assorted files, half round, 250mm, including handles. | Set | 1 |  | 0
ME 3.12 | Spare file handles, 100 x 27 mm. | No. | 5 |  | 0
ME 3.13 | 3 suitable feelers, in tenths of millimetre and 150 mm long. | Set | 1 |  | 0
ME 3.14 | Mechanic's hammer, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.15 | Carpenter's claws 1/5, 1/2. 1 and 2 kg. | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
0
ME 3.16 | Sledge hammer, 3 kg. | No. | 2 |  | 0
ME 3.17 | Rubber mallet, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.18 | Hooks to remove packings. | No. | 2 |  | 0
ME 3.19 | Grease gun, 200 ml minimum. | No. | 1 |  | 0
ME 3.20 | Oiler, approx. 200 ml capacity, trigger operated, 150mm long flexible spout. | No. | 1 |  | 0
ME 3.21 | Carpenter's pincers, 200 mm jointer's shouldered type. | No. | 2 |  | 0
ME 3.22 | Adjustable pliers, 300 mm and 400mm. | Set | 1 |  | 0
ME 3.23 | Round nose pliers, 150 mm. | No. | 1 |  | 0
ME 3.24 | Puller set, inside-outside, to suit bearings and couplings incorporated in the equipment. | No. | 1 |  | 0
ME 3.25 | Punches, 1 - 10 mm. | Set | 1 |  | 0
ME 3.26 | Reamer, 7 - 17 mm. | Set | 1 |  | 0
ME 3.27 | Hack Saw, adjustable tubular frame, length 250-300mm, including 20 Nos. of spare blades. | No. | 1 |  | 0
ME 3.28 | Sockets, numbers ranging from 2 to 38, with ratchets and handles | Set | 1 |  | 0
ME 3.29 | Scraper spoon, flat and triangular type. | Set | 1 |  | 0
ME 3.30 | Snips, tin plate cutter, 300 mm. | No. | 1 |  | 0
ME 3.31 | Shears, universal, 200 mm. | No. | 1 |  | 0
ME 3.32 | Wrench, chain 16 to 100 mm capacity. | No. | 1 |  | 0
ME 3.33 | Wrench, pipe 300/400/600/900 mm. | No. | 2 |  | 0
ME 3.34 | Wrench, allen set, numbers ranging from 2 to 38. | No. | 1 |  | 0
ME 3.35 | Open ended spanner, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.36 | Ring spanners, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.37 | Hexagon nut drive spanners, 2-14 mm, metric size. | Set | 1 |  | 0
MISCELLANEOUS TOOLS
MT 5.1 | Contractor's pick axe with point and chisel steel end, length 800 mm | No. | 2 |  | 0
MT 5.2 | Steel hoe, blade width 200 mm, 1.5 kg complete with good wooden handle | No. | 2 |  | 0
MT 5.3 | Seamless pressed tray wheelbarrow, steel frame, with pneumatic wheels, 80 litres | No. | 2 |  | 0
MT 5.4 | Steel Slashers | No. | 5 |  | 0
MT 5.5 | 33CC 2-Cycle Petrol-Powered engine Straight Shaft Attachment Capable String Lawn Trimmer with 17-inch cutting path (including 10No. replacement trimmer lines) | No. | 1 |  | 0
MT 5.6 | Steel rakes | No. | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA ME-4/1 |  |  |  | 0
| Collection, Page GPA ME-4/2 |  |  |  | 0
| Collection, Page GPA ME-4/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## GPA S-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA S-1
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - BOYS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 43.4 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 75 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 187 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 12 |  | 0
|  |  |  | Carried to Collection | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA S-1.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
GPA S-1.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
GPA S-1.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
GPA S-1.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
GPA S-1.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
GPA S-1.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
GPA S-1.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
GPA S-1.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
GPA S-1.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Water and Drainage
GPA S-1.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
GPA S-1.11 | Construct Urinal facility complete with floor trap, domical removable cast iron grating, gulley trap and including OD 110 uPVC PN 6 drainage pipework to soak away pit | sum | 1 |  | 0
GPA S-1.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
GPA S-1.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
GPA S-1.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
GPA S-1.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA S-1/1 |  |  |  | 0
| Collection, Page GPA S-1/2 |  |  |  | 0
| Collection, Page GPA S-1/3 |  |  |  | 0
| Collection, Page GPA S-1/4 |  |  |  | 0
| Collection, Page GPA S-1/5 |  |  |  | 0
| Collection, Page GPA S-1/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## GPA S-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA S-2
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - GIRLS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 20.3 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
|  |  |  | Carried to Collection | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 80 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 193 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 13 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA S-2.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 6 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
GPA S-2.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
GPA S-2.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
GPA S-2.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
GPA S-2.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
GPA S-2.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
GPA S-2.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
GPA S-2.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
GPA S-2.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
GPA S-2.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
GPA S-2.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
GPA S-2.12 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm dia chromium plated pillar taps | nr | 1 |  | 0
GPA S-2.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
GPA S-2.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
GPA S-2.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
GPA S-2.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
GPA S-2.17 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA S-2/1 |  |  |  | 0
| Collection, Page GPA S-2/2 |  |  |  | 0
| Collection, Page GPA S-2/3 |  |  |  | 0
| Collection, Page GPA S-2/4 |  |  |  | 0
| Collection, Page GPA S-2/5 |  |  |  | 0
| Collection, Page GPA S-2/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## GPA S-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
GASPA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. GPA S-3
DESCRIPTION: 4 STANCE PUBLIC WATERBORNE TOILETS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 110 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 37.6 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E323 | Depth 0.5 - 1 m | m³ | 37.2 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to toilet block and compacted to 98% MOD AASHTO | m³ | 5.2 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 4.2 |  | 0
E647 | 200mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 16.5 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 42 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F251 | 10mm aggregate | m³ | 8.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete for footings, grade C15 of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 2.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522 | Thickness 150-300mm | m³ | 4.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 3 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.7 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.4 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 9.6 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | kg | 150 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 28.3 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 17.7 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 47 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 21 |  | 0
|  |  |  | Carried to Collection | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 4 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 67 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.7 |  | 0
Masonry
External quality weather guard paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 49 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 79 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153.1 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 78.1 |  | 0
W153.2 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a steel float | m² | 49 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 78.1 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.3 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16.5 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 49 |  | 0
MISCELLANEOUS WORKS
Structural
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, stays, plugging and fixing to wall
GPA S-3.1 | Top hung double leaf hinged windows overall size 3450 x 1150mm high comprising of 3mm thick mild steel panes welded on a 25x25x3mm thick angle frame and epoxy coated colour blue | nr | 1 |  | 0
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
GPA S-3.2 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
GPA S-3.4 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
GPA S-3.5 | Single leaf door overall size 1000 x 2100mm high | nr | 3 |  | 0
Roofing
GPA S-3.6 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, metal lathe ceiling and eaves, and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 34.7 |  | 0
Building Finishes
GPA S-3.7 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
GPA S-3.8 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
GPA S-3.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 10no. toilet paper holders, installation of floor drains with associated pipework and fitting s connected to soak pit, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
GPA S-3.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
GPA S-3.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
GPA S-3.12 | Construct Urinal facility with perforated DN 20 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap | sum | 1 |  | 0
GPA S-3.13 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm diameter chromium plated pillar taps | sum | 1 |  | 0
GPA S-3.14 | Provide materials and construct a hand washing facility complete with wash hand basins, DN 13/20 GI/PPR plumbing pipework, uPVC drainage pipework, all fittings, gulley and bottle traps, valves, 13mm diameter chromium plated pillar taps, waste outlet gratings, all accessories, including single low level wash hand basin for disabled person's usage; as per specifications and drawings and to the Engineer's approval | nr | 2 |  | 0
GPA S-3.15 | Excavate and construct standard manholes in 200mm thick blockwork, internal depth not exceeding 1.0m, bonded in concrete mortar(1:5) and rendered internally with concrete mortar (1:4), concrete benching, complete with and including CI frame and cover, and interconnecting OD 110mm pvc drain pipes to toilet block | nr | 4 |  | 0
GPA S-3.16 | Supply and Install OD 110 mm uPVC PN 6 drainage pipework to BS 4660, complete with spigot and socket joints, all fittings; from toilet block to Septic Tank and Soak Pit | m | 78 |  | 0
GPA S-3.17 | Excavate and construct Septic Tank of effective capacity 15.4m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty cast iron manhole covers | Sum | 1 |  | 0
GPA S-3.18 | Excavate and construct 2500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
GPA S-3.19 | Supply and install squatting type low level water closet suite complete with WC pan, heavy duty cistern complete with anti-vandal cage, flush pipe, connected to nearest manhole; all to the Engineer's satisfaction | nr | 3 |  | 0
GPA S-3.20 | Supply and install seat type low level water closet suite complete with WC pan, heavy duty cistern, flush pipe complete with anti-vandal cage, connected to nearest manhole; all to the Engineer's satisfaction | nr | 2 |  | 0
GPA S-3.31 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
Power Supply to Waterborne Toilet
GPA S-3.32 | Provisional for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page GPA S-3/1 |  |  |  | 0
| Collection, Page GPA S-3/2 |  |  |  | 0
| Collection, Page GPA S-3/3 |  |  |  | 0
| Collection, Page GPA S-3/4 |  |  |  | 0
| Collection, Page GPA S-3/5 |  |  |  | 0
| Collection, Page GPA S-3/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 2 | 0 | 0
|  |  |  | Carried to Summary | 0

## Summary-Nyakabale
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
CONSTRUCTION OF NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
Engineer's Estimate
Grand Summary
Bill No | Description | Investment Costs
UShs
WATER SUPPLY AND EQUIPMENT
NYA W-1 | Borehole Pump Station (DWD 77382) | 0
NYA W-2 | Borehole Pump Station (DWD 77383) | 0
NYA W-3 | Borehole Pumping Mains (DWD 77382) | 0
NYA W-4 | Borehole Pumping Mains (DWD 77383) | 0
NYA W-5 | Storage Reservoir and Site Works | 0
NYA W-6 | Distribution Network | 0
NYA W-7 | Intensification Network | 0
NYA W-8 | Chemical House (1No.) | 0
NYA W-9 | Borehole Guard / Attendant House (2No.) | 0
NYA W-10 | Water Office Block | 0
NYA ME-1 | Mechanical & Electrical Works (DWD 77382) | 30000000
NYA ME-2 | Mechanical & Electrical Works (DWD 77383) | 30000000
NYA ME-3 | Mechanical & Electrical Works (Water Office) | 0
NYA ME-4 | Mechanical & Electrical Works (Chemical House - 1No.) | 0
NYA ME-5 | Tools and Equipment | 0
SANITATION
NYA S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
NYA S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
NYA S-3 | 4 Stance Waterborne Toilet - 1No. | 0
0
| Sub-Total 1 | 60000000
| Allow for 10% contingency | 6000000
| Sub-Total 2 | 66000000
| Allow for 18% VAT | 11880000
| GRAND TOTAL | 77880000

## NYA W-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-1
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77382
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
15000
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 49 |  | 0
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 33.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to pump house area and compacted to 98% MOD AASHTO | m³ | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.9 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 7.9 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 213 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.9 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and generator plinth of the following thickness
F622 | Thickness 150-300mm | m³ | 38 |  | 0
Suspended Slabs
Placing reinforced concrete, grade C25, for false slab (ceiling) of the following thickness
F631 | Thickness not exceeding 150mm | m³ | 1.9 |  | 0
|  |  |  | Carried to Collection | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to floor and pump house of the following width
G214 | Width: 0.4-1.22m; to false slab soffits | m² | 38.6 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244.1 | Width: 0.4-1.22m; to floor and generator plinth | m² | 5.7 |  | 0
G244.2 | Width: 0.4-1.22m; to sides of the ring beam | m² | 4.5 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 156 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 26.5 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of Pump Stations | m2 | 40.6 |  | 0
PIPEWORK - FITTINGS AND VALVES
Pipework and Fittings for DWD 77382 with yield of 34.0m3/hr
Ductile spun iron/ steel pipes with spigot and socket type joints and cement mortar linings, 100 mm ND DI PN16 Pipes, all to EN 545 and including approved rubber gaskets, trench excavation, lowering, laying and jointing of pipes; not in trenches including casting in as required
All pipe specials are annotated and specified on the pump station drawing. The code indicated refers to the code on the drawing.
Bends
J311.1 | BH11 - DN 100mm x 45deg flanged small radius bend | No | 2 |  | 0
J311.2 | BH23 - DN 100mm x 90deg flanged small radius bend | No | 2 |  | 0
|  |  |  | Carried to Collection | 0
Junctions and Branches
J312.1 | BH6 - DN 100mm flanged tee with 25mm female threaded branch | No | 2 |  | 0
Adaptors
J351.1 | BH8 - DN 15mm diam. Hexagon nipple | No | 1 |  | 0
J351.2 | BH16 - DN 25mm diam. Hexagon nipple | No | 2 |  | 0
J351.3 | BH2 - DN100mm Detachable / Maxi Flanged coupling | No | 2 |  | 0
Glands
J361.1 | BH4 - DN 100mm Double-flexible rubber pipe flanged coupling | No | 2 |  | 0
Straight specials - DN 100 mm pipe with fittings
J381.1 | BH1 - plain threaded both ends, nominally 3000mm long, cut to suit on site | No | 1 |  | 0
J381.2 | BH3 - DN100 Steel/DI/HDPE/uPVC PN16 riser pipes from submersible pump to top plate; complete to match pump outlet size and pumphouse pipe work | m | 100 |  | 0
J381.3 | BH12 - flanged both ends, 800mm f/f | No | 1 |  | 0
J381.4 | BH14 - flanged both ends, 400mm f/f | No | 1 |  | 0
J381.5 | BH19 - flanged both end, nominally 1500mm, cut-to-suit on site | No | 1 |  | 0
Gate Valves
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | DN 100mm | No | 2 |  | 0
Air Valves
BH 18- Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 50 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J861.1 | DN 100mm | No | 1 |  | 0
|  |  |  | Carried to Collection | 0
Pressure Gauge
J891.1 | BH10 - WIKA pressure gauge, DN 100mm case, glycerine filled with 15mm male thread | No | 1 |  | 0
Non-Return Valves
BH 15 - Flanged Non return Valves shall confirming to BS EN 12334:2001, flanges to EN 1092, all to PN16 the follwing pipe sizes.
J861.1 | DN 100mm | No | 1 |  | 0
Bulk Flow Meter
J991.1 | BH13 - flanged DN 100mm MEINECKE Cosmos WP bulk water meter | No | 1 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Isolated pipe supports
L811 | Pipe support 1 - mass concrete 200mm x 200mm x 600mm high, Class 20/20, complete with shuttering, to pipes | nr | 1 |  | 0
L812 | Pipe support 2 - mass concrete 200mm x 200mm x nominal 500mm high, Class 20/20, complete with shuttering, to valve (BH15) and tee (BH6) | nr | 2 |  | 0
L813 | Pipe support 3 - mass concrete 500mm x300mm x nominal 500mm high, Class 20/20, complete with shuttering, to bend | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 4302 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 1291 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 10 |  | 0
PAVINGS
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 36 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces, as detailed in the drawings, for walls of the following thickness
U521 | 230 mm thick | m2 | 99.2 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.9 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 34.6 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 61.2 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 26.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 25.7 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 38.6 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 50.6 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 48.4 |  | 0
MISCELLANEOUS WORKS
Roofing
NYA W-1.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board and all roofing timber, eave closing, gauge 26 prepainted GCI resin sheeting and ridges | m² | 38.7 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories, including aluminium mosquito proof wire gauze welded to mild steel frames in 300mm high permanent vents
NYA W-1.2 | Single leaf steel door, size 900 x 2400mm with 700mm high 4mm thick glass panes and burglar proofing; complete | nr | 1 |  | 0
NYA W-1.3 | Double leaf door overall size 1800 x 2400mm high filled in with 20 x 2mm thick mild steel square hollow section grating welded to door, complete | nr | 1 |  | 0
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
NYA W-1.4 | Steel frame glazed window, 1200mm by 2000mm clear opening; include frame, glazing, all iron mongery | nr | 3 |  | 0
Building Finishes
NYA W-1.5 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-1/1 |  |  |  | 0
| Collection, Page NYA W-1/2 |  |  |  | 0
| Collection, Page NYA W-1/3 |  |  |  | 0
| Collection, Page NYA W-1/4 |  |  |  | 0
| Collection, Page NYA W-1/5 |  |  |  | 0
| Collection, Page NYA W-1/6 |  |  |  | 0
| Collection, Page NYA W-1/7 |  |  |  | 0
| Collection, Page NYA W-1/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-2
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77383
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
15000
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 49 |  | 0
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 33.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to pump house area and compacted to 98% MOD AASHTO | m³ | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.9 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 7.9 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 213 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.9 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and generator plinth of the following thickness
F622 | Thickness 150-300mm | m³ | 38 |  | 0
Suspended Slabs
Placing reinforced concrete, grade C25, for false slab (ceiling) of the following thickness
F631 | Thickness not exceeding 150mm | m³ | 1.9 |  | 0
|  |  |  | Carried to Collection | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to floor and pump house of the following width
G214 | Width: 0.4-1.22m; to false slab soffits | m² | 38.6 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244.1 | Width: 0.4-1.22m; to floor and generator plinth | m² | 5.7 |  | 0
G244.2 | Width: 0.4-1.22m; to sides of the ring beam | m² | 4.5 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 156 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 26.5 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of Pump Stations | m2 | 40.6 |  | 0
PIPEWORK - FITTINGS AND VALVES
Pipework and Fittings for DWD 77383 with yield of 10.0m3/hr
Ductile spun iron/ steel pipes with spigot and socket type joints and cement mortar linings, 65 mm ND DI PN16 Pipes, all to EN 545 and including approved rubber gaskets, trench excavation, lowering, laying and jointing of pipes; not in trenches including casting in as required
All pipe specials are annotated and specified on the pump station drawing. The code indicated refers to the code on the drawing.
Bends
J311.1 | BH11 - DN 65mm x 45deg flanged small radius bend | No | 2 |  | 0
J311.2 | BH23 - DN 65mm x 90deg flanged small radius bend | No | 2 |  | 0
|  |  |  | Carried to Collection | 0
Junctions and Branches
J312.1 | BH6 - DN 65mm flanged tee with 25mm female threaded branch | No | 2 |  | 0
Adaptors
J351.1 | BH8 - DN 15mm diam. Hexagon nipple | No | 1 |  | 0
J351.2 | BH16 - DN 25mm diam. Hexagon nipple | No | 2 |  | 0
J351.3 | BH2 - OD 75 x 2 1/2" Detachable / Maxi Flanged coupling | No | 2 |  | 0
Glands
J361.1 | BH4 - DN 65mm Double-flexible rubber pipe flanged coupling | No | 2 |  | 0
Straight specials - DN 65 mm pipe with fittings
J381.1 | BH1 - plain threaded both ends, nominally 3000mm long, cut to suit on site | No | 1 |  | 0
J381.2 | BH3 - DN65 Steel/DI/uPVC/HDPE PN16 riser pipes from submersible pump to top plate; complete to match pump outlet size and pumphouse pipe work | m | 100 |  | 0
J381.3 | BH12 - flanged both ends, 800mm f/f | No | 1 |  | 0
J381.4 | BH14 - flanged both ends, 400mm f/f | No | 1 |  | 0
J381.5 | BH19 - flanged both end, nominally 1500mm, cut-to-suit on site | No | 1 |  | 0
Gate Valves
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | DN 65mm | No | 2 |  | 0
Air Valves
BH 18- Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 50 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J861.1 | DN 65mm | No | 1 |  | 0
|  |  |  | Carried to Collection | 0
Pressure Gauge
J891.1 | BH10 - WIKA pressure gauge, DN 65mm case, glycerine filled with 15mm male thread | No | 1 |  | 0
Non-Return Valves
BH 15 - Flanged Non return Valves shall confirming to BS EN 12334:2001, flanges to EN 1092, all to PN16 the follwing pipe sizes.
J861.1 | DN 65mm | No | 1 |  | 0
Bulk Flow Meter
J991.1 | BH13 - flanged DN 65mm MEINECKE Cosmos WP bulk water meter | No | 1 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Isolated pipe supports
L811 | Pipe support 1 - mass concrete 200mm x 200mm x 600mm high, Class 20/20, complete with shuttering, to pipes | nr | 1 |  | 0
L812 | Pipe support 2 - mass concrete 200mm x 200mm x nominal 500mm high, Class 20/20, complete with shuttering, to valve (BH15) and tee (BH6) | nr | 2 |  | 0
L813 | Pipe support 3 - mass concrete 500mm x300mm x nominal 500mm high, Class 20/20, complete with shuttering, to bend | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 60 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 18 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 10 |  | 0
PAVINGS
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 36 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces, as detailed in the drawings, for walls of the following thickness
U521 | 230 mm thick | m2 | 99.2 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.9 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 34.6 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 61.2 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 26.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 25.7 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 38.6 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 50.6 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 48.4 |  | 0
MISCELLANEOUS WORKS
Roofing
NYA W-2.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board and all roofing timber, eave closing, gauge 26 prepainted GCI resin sheeting and ridges | m² | 38.7 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories, including aluminium mosquito proof wire gauze welded to mild steel frames in 300mm high permanent vents
NYA W-2.2 | Single leaf steel door, size 900 x 2400mm with 700mm high 4mm thick glass panes and burglar proofing; complete | nr | 1 |  | 0
NYA W-2.3 | Double leaf door overall size 1800 x 2400mm high filled in with 20 x 2mm thick mild steel square hollow section grating welded to door, complete | nr | 1 |  | 0
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
NYA W-2.4 | Steel frame glazed window, 1200mm by 2000mm clear opening; include frame, glazing, all iron mongery | nr | 3 |  | 0
Building Finishes
NYA W-2.5 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-2/1 |  |  |  | 0
| Collection, Page NYA W-2/2 |  |  |  | 0
| Collection, Page NYA W-2/3 |  |  |  | 0
| Collection, Page NYA W-2/4 |  |  |  | 0
| Collection, Page NYA W-2/5 |  |  |  | 0
| Collection, Page NYA W-2/6 |  |  |  | 0
| Collection, Page NYA W-2/7 |  |  |  | 0
| Collection, Page NYA W-2/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-3
DESCRIPTION: BOREHOLE PUMPING MAINS DWD 77382
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 9172 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 6 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 4 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS EN1452, with flexible joints to BS EN14814 all to PN16, OD160mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 7643 |  | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Flanged adaptor to fit uPVC pipe spigots to BS 3505, flanges to BS 4505, all to PN16, and of the following sizes
J351.1 | 150 mm ND | nr | 22 |  | 0
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.1 | 150 mm ND | nr | 5 |  | 0
Ductile Iron all flanged 22.5 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.2 | 150 mm ND | nr | 6 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 25 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 150 mm ND | nr | 2 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valves, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes;all to PN16
J911.1 | 150 mm ND | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 2 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 2 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 1 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.1 | Diameter not exceeding 300 mm ND | m | 24 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes | nr | 20 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 171.9675 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 11 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 100 mm ND | m | 6393 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 100 mm ND | m | 1000 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 100 mm ND | m | 250 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-3/1 |  |  |  | 0
| Collection, Page NYA W-3/2 |  |  |  | 0
| Collection, Page NYA W-3/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-4
DESCRIPTION: BOREHOLE PUMPING MAINS DWD 77383
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 6539 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 3 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
Plastic Pipes
Plastic Pressure Pipes
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 16, OD 90mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 5449 |  | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN16, and of the following spigot sizes
J351.1 | OD 90 mm X 3" | nr | 8 |  | 0
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.1 | 80 mm ND | nr | 4 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 80 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 25 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 80 mm ND | nr | 1 |  | 0
Washouts
Type 2 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valves, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes;all to PN16
J911.1 | 80 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 1 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 1 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 4 |  | 0
|  |  |  | Carried to Collection | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.1 | Diameter not exceeding 300 mm ND | m | 24 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes | nr | 14 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 122.6025 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 4 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 100 mm ND | m | 4199 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 100 mm ND | m | 1000 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 100 mm ND | m | 250 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-4/1 |  |  |  | 0
| Collection, Page NYA W-4/2 |  |  |  | 0
| Collection, Page NYA W-4/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-5
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-5
DESCRIPTION: STORAGE RESERVOIR AND SITE WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for works | m2 | 625 |  | 0
EARTHWORKS
General Excavation
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 16.5 |  | 0
Excavation for foundations
Ordinary Soil
Excavation for foundations (stub columns), in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth 0.5-1m | m³ | 27 |  | 0
E324 | Depth 1-2m | m³ | 36 |  | 0
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5 - 1.0 m | m³ | 2.7 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces in the following materials
E522 | Material other than topsoil, rock or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 72 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 13.1 |  | 0
E533 | Rock | m³ | 2.7 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 13.9 |  | 0
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to foundations and compacted to 98% MOD AASHTO | m³ | 2.7 |  | 0
Filling Ancillaries
Trimming of Filled Surfaces
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 72 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 425 |  | 0
Provision of Hardcore
E810 | Provision and placement of 300mm thick hardcore base for the tank footings | m² | 27 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F131 | 10 mm aggregate | m³ | 1.4 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F151 | 10 mm aggregate | m³ | 13.1 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, grade C15, of the following thickness
F512 | Thickness 150-300mm | m³ | 1.4 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete, grade C25, for column base footings of the following thickness
F522 | Thickness 300-500 mm | m³ | 10.8 |  | 0
Columns
Placing reinforced concrete, grade C25, for columns of the following thickness
F522 | Thickness 300-500 mm | m³ | 2.3 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G245 | Width exceeding 1.22m | m² | 51.8 |  | 0
Reinforcement
High Yield Steel
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 1634 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G812 | With steel float finish | m² | 23 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK - PIPES
Plastic Drain Pipes
uPVC drain pipes, conforming to BS EN1452, ith flexible joints to BS EN14814, 160 mm OD PN 6, laid in trench to the following depths
I512 | Depth not exceeding 1.5m | m | 30 |  | 0
PIPEWORK - FITTINGS AND VALVES
Cast or Spun Iron Pipe Fittings
external epoxy coated to AWWA C213
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.1 | 80 mm ND | nr | 1 |  | 0
J311.2 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.3 | 80 mm ND | nr | 1 |  | 0
J311.4 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.5 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.6 | 80 mm ND | nr | 2 |  | 0
J311.7 | 150 mm ND | nr | 1 |  | 0
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 150/80 mm ND | nr | 1 |  | 0
Double Collars
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J341.1 | 150 mm ND | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 16, and of the following sizes
J341.2 | 80 mm ND | nr | 1 |  | 0
J341.3 | 150 mm ND | nr | 1 |  | 0
Adaptors
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 2 |  | 0
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN16, and of the following sizes
J351.1 | 150 mm ND | nr | 1 |  | 0
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN16, and of the following spigot sizes
J351.1 | OD 90 mm X 3" | nr | 1 |  | 0
Bellmouths
Flanged bellmouth to ISO 2531, flanges to ISO 2441, of the following sizes all to PN 10
J372.1 | 150 mm ND | nr | 1 |  | 0
Straight Specials
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 10 and of the following sizes
J381.1 | 80 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.2 | 80 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.3 | 150 mm ND not exceeding 0.6m | nr | 4 |  | 0
J381.4 | 150 mm ND not exceeding 1.0m | nr | 3 |  | 0
J381.5 | 150 mm ND not exceeding 3.0m | nr | 3 |  | 0
J381.6 | 150 mm ND not exceeding 6.0m | nr | 2 |  | 0
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 16 and of the following sizes
J381.7 | 80 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.8 | 80 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.9 | 80 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.10 | 80 mm ND not exceeding 6.0m | nr | 1 |  | 0
J381.11 | 150 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.12 | 150 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.13 | 150 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.14 | 150 mm ND not exceeding 6.0m | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491.1 | 150 mm ND | nr | 1 |  | 0
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 80 mm ND | nr | 1 |  | 0
J811.2 | 150 mm ND | nr | 1 |  | 0
Ball Float Valves
Flanged Balanced ball float valve, flanges to BS 4505, all to PN16
J891.1 | 150 mm ND | nr | 1 |  | 0
Bulk Flow Meter
"Woltman" Helix Type Bulk Flow Meter inclusive of all couplings, adaptors, steel pipe distance pieces, CI valves, thrust blocks, etc and all other fittings to make the installation complete, as specified, all fittings to PN 10, including lockable vented blockwork chamber with cast in valve surface boxes, and on the following main pipe sizes
J991.1 | 150 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Manholes
Blockwork Manhole
Blockwork chamber complete with C20 concrete base, vented lockable manhole cover, valve surface boxes, galvanised step irons, as specified in the drawings, and of the following depths
K171 | Depth not exceeding 1.5m | nr | 2 |  | 0
Other Chambers
In situ Concrete Chambers
Washout out fall structure, complete including flap valve, all fittings and pipework necessary to complete installation, as specified in drawings, and of the following depths; all fittings and pipework to PN 10
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Supply and construct grouted stone pitching using mortar mix 1:4, include 50mm thick coping using 1:2:4 concrete mix on top of the stone pitching of same width as the wall thickness for drains of cross section
K 491 | Cross section area 0.5-1.0m2 | m | 20 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 1 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for bulk meters | nr | 1 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 300 mm ND | m | 20 |  | 0
MISCELLANEOUS WORKS
Supply and Install cold pressed galvanised steel sectional tank with external flanges and pitched cover with 1No. 1m wide access man way, 10m high tower, water level indicator (scale in cubic metres) and plates with inlet, outlet, washout and overflow connection complete with access points, ventilators (4 nr), walkway, handrailing, and internal and external access ladders with safety hoops, inclusive of painting, finishes and all necessary accessories to installation complete as specified and detailed in the drawings; to the Engineer's satisfaction. All tank accessories shall be of hot dipped galvanised steel.
NYA W-5.1 | Reservoir: 150m3 nominal capacity erected on a 15m high tower | nr | 1 |  | 0
NYA W-5.2 | Supply and Installation of a 15m high steel tower | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 1524 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 457 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-5/1 |  |  |  | 0
| Collection, Page NYA W-5/2 |  |  |  | 0
| Collection, Page NYA W-5/3 |  |  |  | 0
| Collection, Page NYA W-5/4 |  |  |  | 0
| Collection, Page NYA W-5/5 |  |  |  | 0
| Collection, Page NYA W-5/6 |  |  |  | 0
| Collection, Page NYA W-5/7 |  |  |  | 0
| Collection, Page NYA W-5/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-6
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-6
DESCRIPTION: DISTRIBUTION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 16932 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 3 |  | 0
D320 | Diameter 500 mm -1 m | nr | 3 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to all to PN10, OD160mm, laid in trench to the following depths
I512.1 | Depth not exceeding 1.5m | m | 742 |  | 0
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to BS4346 all to PN10, OD110mm, laid in trench to the following depths
I512.2 | Depth not exceeding 1.5m | m | 5767 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 90mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 1245 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 75mm, laid in trench to the following depths
I712.2 | Depth not exceeding 1.5m | m | 417 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 63mm, laid in trench to the following depths
I712.3 | Depth not exceeding 1.5m | m | 1183 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 50mm, laid in trench to the following depths
I712.4 | Depth not exceeding 1.5m | m | 4755 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 150/150 mm ND | nr | 1 |  | 0
J321.2 | 150/50 mm ND | nr | 1 |  | 0
J321.3 | 100/80 mm ND | nr | 1 |  | 0
J321.4 | 100/50 mm ND | nr | 1 |  | 0
J321.5 | 80/65 mm ND | nr | 1 |  | 0
J321.6 | 80/40 mm ND | nr | 1 |  | 0
J321.7 | 65/40 mm ND | nr | 2 |  | 0
J321.8 | 50/40 mm ND | nr | 2 |  | 0
Tapers
Ductile iron all flanged concentric taper to EN 545, flanges to EN 1092-2 all to PN10, cement mortar lined, and of the following sizes
J331.1 | 150/100 mm ND | nr | 2 |  | 0
J331.2 | 100/80 mm ND | nr | 1 |  | 0
J331.3 | 100/50 mm ND | nr | 1 |  | 0
J331.4 | 80/65 mm ND | nr | 1 |  | 0
J331.5 | 65/50 mm ND | nr | 1 |  | 0
J331.6 | 65/40 mm ND | nr | 1 |  | 0
J331.7 | 50/40 mm ND | nr | 3 |  | 0
Adaptors
Flanged adaptor to fit uPVC pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 2 |  | 0
J351.2 | 100 mm ND | nr | 6 |  | 0
Plastic Pipe Fittings
Bends
uPVC 22.5 degree bends with push-fit joint for use with uPVC pipes, to EN 1401, all to PN 10, and of the following sizes
J311.1 | 150mm ND | nr | 2 |  | 0
J311.2 | 100 mm ND | nr | 3 |  | 0
HDPE 90 degree bends for use with HDPE pipes, to EN12201, all to PN 10, and of the following sizes
J311.3 | 40mm ND | nr | 1 |  | 0
Adaptors
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.1 | OD 90 mm X 3" | nr | 4 |  | 0
J651.2 | OD 75 mm X 2 1/2" | nr | 5 |  | 0
J651.3 | OD 63 mm X 2" | nr | 5 |  | 0
J651.4 | OD 50 mm X 1 1/2" | nr | 9 |  | 0
|  |  |  | Carried to Collection | 0
End caps
Compression HDPE end caps to fit uPVC spigots, to EN 12201 and to PN 10 of the following spigot sizes
J691.1 | ND 65 mm | nr | 1 |  | 0
J691.2 | ND 50 mm | nr | 1 |  | 0
J691.3 | ND 40 mm | nr | 7 |  | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 3 |  | 0
J811.2 | 100 mm ND | nr | 2 |  | 0
J811.3 | 80 mm ND | nr | 2 |  | 0
J811.4 | 65 mm ND | nr | 4 |  | 0
J811.5 | 50 mm ND | nr | 4 |  | 0
J811.6 | 40 mm ND | nr | 5 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 25 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN10, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 100 mm ND | nr | 1 |  | 0
J862.2 | 40 mm ND | nr | 1 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 100 mm ND | nr | 1 |  | 0
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 80 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 2 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 20 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 8 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 56 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 20 |  | 0
K820.2 | Marker posts for air valves | nr | 2 |  | 0
K820.3 | Marker posts for wash outs | nr | 2 |  | 0
K820.4 | Marker posts for pipes | nr | 36 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 317.4525 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 6 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 12109 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-6/1 |  |  |  | 0
| Collection, Page NYA W-6/2 |  |  |  | 0
| Collection, Page NYA W-6/3 |  |  |  | 0
| Collection, Page NYA W-6/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA W-7
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-7
DESCRIPTION: INTENSIFICATION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | m2 | 14400 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
PIPEWORK-PIPES
Plastic Pressure Pipes- Distribution
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 40 mm, laid in trench to the following depths
I711.1 | Depth not exceeding 1.5m | m | 3830 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 32 mm, laid in trench to the following depths
I711.2 | Depth not exceeding 1.5m | m | 3830 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 25 mm, laid in trench to the following depths
I711.3 | Depth not exceeding 1.5m | m | 3830 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD32 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 2 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
Make a connection for OD25 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 2 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 8 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
K731 | Not exceeding 300 mm ND | m | 56 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 258.525 |  | 0
|  |  |  | Carried to Collection | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 9490 |  | 0
Pipe surrounds, of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds, of mass concrete , for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
Consumer Connections
Make DN20 consumer connection to the distribution main (maximum 100m), complete, inclusive of excavation, backfill, saddle clamp, ferrule, taps,domestic water meter and all fittings for connection to GI or HDPE service pipes, as detailed in the drawings, for the following mains sizes and all to PN10
J891.1 | ND 40 mm | nr | 100 |  | 0
J891.2 | ND 50 mm | nr | 100 |  | 0
J891.3 | ND 65 mm | nr | 100 |  | 0
J891.4 | ND 100 mm | nr | 80 |  | 0
J891.5 | ND 150 mm | nr | 80 |  | 0
Public Stand Posts
Construct a double faucet Stand Post complete as in drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fitings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN 10 (service line measured separately under items I712)
L999.1 | ND 20 mm (3/4") | nr | 15 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-7/1 |  |  |  | 0
| Collection, Page NYA W-7/2 |  |  |  | 0
| Collection, Page NYA W-7/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## NYA W-8
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-8
DESCRIPTION: CHEMICAL HOUSE (1No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5 - 1.0 m | m³ | 26.7 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 0.8 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 25.4 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 2.4 |  | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 15.6 |  | 0
E533 | Rock | m³ | 0.8 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling Ancillaries
Filling
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated granular material other than topsoil, rock or artificial hard material compacted to 98% MOD AASHTO | m³ | 11.1 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.1 |  | 0
|  |  |  | Carried to Collection | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 6.3 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 40.1 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 3.8 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.3 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 4.35 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.3 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C25, for floor slab, stairs and tank base of the following thickness
F622 | Thickness 150-300mm | m³ | 3.3 |  | 0
Beams
Placing reinforced concrete grade C25, for ring beam of the following cross-sectional area
F562 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.05 |  | 0
|  |  |  | Carried to Collection | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G212 | Width: 0.1-0.2m | m² | 5.1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G243 | Width: 0.2-0.4m | m² | 20 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS 4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 304 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 22.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 22.5 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U523 | 200 mm thick | m² | 90 |  | 0
Permanent Vents
Construct dense concrete pre-cast louvered blockwork vents to BS 7263, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U590.1 | 1500mm x 1200mm (W x H) | nr | 1 |  | 0
U590.2 | 2600mm x 1200mm (W x H) | nr | 3 |  | 0
|  |  |  | Carried to Collection | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.7 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 12.6 |  | 0
Emulsion Paint
Masonry
Internal quality emulsion paint, two coats, to the following smooth masonry surfaces, include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 71 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 22.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 22.2 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 20.7 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 44 |  | 0
|  |  |  | Carried to Collection | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 44 |  | 0
MISCELLANEOUS WORKS
Doors
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA W-8.1 | 900mm x 2400mm (W x H including 300mm wood pvo) | nr | 2 |  | 0
Roofing
NYA W-8.2 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI resin sheeting and ridges; the GCI sheet should be resin bonded or with other protection against corrosion by Chlorine | m² | 35 |  | 0
NYA W-8.3 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 20.7 |  | 0
Building Finishes
NYA W-8.4 | Chemical house finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 600mm wide C20 concrete splash apron, 2 no. drainage manholes of internal dimension 700x700mm with OD 110 PVC drainage pipework to soak pit included, 300mm x 1380mm x 100mm thick reinforced concrete doser plinth cover slabs over inlet pipe channel, etc complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
NYA W-8.5 | Supply, lay and fix inlet pipes, valves and fittings; including ball valves and flowmeter; from the outlet pipe of the nearby reservoir tank to the water tank of size OD32mm, all pipe and fittings in HDPE/uPVC/PPR to PN 10 as approved by the Engineer | Sum | 1 |  | 0
NYA W-8.6 | Supply, lay and fix drain pipes, valves and fittings from the tanks to the nearest manhole, as in the drawings, of size OD63mm, all pipe and fittings in HDPE/uPVC/PPR to PN10 as approved by the Engineer; include manhole connection and making good joint | Sum | 1 |  | 0
Mixing Tanks
NYA W-8.7 | Supply and install chlorine generation and dosing PVC tanks of 750 litres capacity as specified and as approved by the Engineer; include complete connection to Electrolytic Disinfecting Machine, Dosing equipment, and incoming DN150mm uPVC pumping Main | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-8/1 |  |  |  | 0
| Collection, Page NYA W-8/2 |  |  |  | 0
| Collection, Page NYA W-8/3 |  |  |  | 0
| Collection, Page NYA W-8/4 |  |  |  | 0
| Collection, Page NYA W-8/5 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## NYA W-9
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-9
DESCRIPTION: GUARD AND PUMP ATTENDANT HOUSE (2No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 38.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to building area and compacted to 98% MOD AASHTO | m³ | 5.45 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 0.79 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 4.75 |  | 0
|  |  |  | Carried to Collection | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.25 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.36 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 2.25 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and steps of the following thickness
F622 | Thickness 150-300mm | m³ | 2.85 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.51 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width: 0.4-1.22m | m² | 1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width: 0.4-1.22m; to sides of the ring beam | m² | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 186 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 16 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 16 |  | 0
BRICKWORK, BLOCKWORK, AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U521.1 | 150 mm thick | m2 | 42.2 |  | 0
U521.2 | 230 mm thick | m² | 33.1 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.4 |  | 0
Masonry
External quality weather guard paint two coats, to the following smooth concrete surfaces; include surface preparation as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 4.5 |  | 0
|  |  |  | Carried to Collection | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 46 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 21 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.2 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 39.3 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 53.7 |  | 0
MISCELLANEOUS WORKS
Roofing
NYA W-9.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes to the Engineer's satisfaction. | m2 | 15 |  | 0
NYA W-9.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600x600mm hardwood access trap door | m² | 14 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
NYA W-9.3 | Mild steel window overall size 1000 x 1100mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
NYA W-9.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
NYA W-9.5 | Single leaf solid steel door, size 900 x 2100mm; complete | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA W-9.6 | 800mm x 2100mm (W x H) | nr | 2 |  | 0
Building Finishes
NYA W-9.7 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
NYA W-9.8 | Supply and install a 1500 litre (1.5m3) Polyethylene tank as Polytank, elevated up to 1.0m above ground level on a rendered brickwork platform, complete with a DN 15mm Brass outlet tap, inlet DN 80 uPVC pipe work from overhead rain water gutters, DN 80 uPVC overflow and drainage pipework to soak pit (inclusive) as per drawings | Sum | 1 |  | 0
NYA W-9.9 | Provide and fix urine diverting squat pans as directed by Engineer | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Plumbing and Drainage
NYA W-9.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
NYA W-9.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
NYA W-9.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
NYA W-9.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
NYA W-9.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
NYA W-9.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-9/1 |  |  |  | 0
| Collection, Page NYA W-9/2 |  |  |  | 0
| Collection, Page NYA W-9/3 |  |  |  | 0
| Collection, Page NYA W-9/4 |  |  |  | 0
| Collection, Page NYA W-9/5 |  |  |  | 0
| Collection, Page NYA W-9/6 |  |  |  | 0
| Cost for 1No. Attendant House |  |  |  | 0
| Total Cost of Attendant Houses | nr | 2 | 0 | 0
|  |  |  | Carried to Summary | 0

## NYA W-10
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA W-10
DESCRIPTION: WATER OFFICE BLOCK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for office premises | ha | 0.1 |  | 0
Trees
Cut and dispose of trees of the following girths; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5-1m | m³ | 52 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 1 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
|  |  | 67 |  | 0
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
|  |  | 1.5 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
|  |  |  | Carried to Collection | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 18 |  | 0
E533 | Rock | m³ | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to office area and compacted to 98% MOD AASHTO | m³ | 26 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.7 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 10 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 24 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 4 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 600 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.2 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 21 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.2 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab of the following thickness
F622 | Thickness 150-300mm | m³ | 17.9 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 3 |  | 0
Columns and Piers
Placing reinforced concrete, grade C25, for columns of the following cross-sectional area
F652 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.12 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to office block of the following width
G213 | Width 0.2 - 0.4m | m² | 7 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G241 | Width not exceeding 0.15m | m² | 6 |  | 0
G243 | Width 0.2 - 0.4m | m² | 33 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 577 |  | 0
|  |  |  | Carried to Collection | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 98 |  | 0
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of office block | m2 | 98 |  | 0
ROADS AND PAVINGS
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO lime stabilised gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 200 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 30 |  | 0
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 48 |  | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U211 | 100 mm thick; Facing Bricks | m2 | 60 |  | 0
U521.1 | 150 mm thick | m2 | 12 |  | 0
U521.2 | 230 mm thick | m2 | 164 |  | 0
Permanent Vents
Dense brickwork vents to BS 7263, jointed with ordinary 1:5 cement mortar above door and window openings, including mosquito mesh, for walls of the following thickness
U589 | 150 - 230 mm thick | m2 | 3 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 8 |  | 0
|  |  |  | Carried to Collection | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 40 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 192 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 60.7 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified.
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
MISCELLANEOUS WORKS
Roofing
NYA W-10.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes connected to 3000m3 rain water polytank placed on 1m high masonry platform & complete with the necessary piping to the Engineer's satisfaction. | m2 | 136.8 |  | 0
NYA W-10.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 136.8 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
NYA W-10.3 | Mild steel window overall size 1500 x 1200mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 4 |  | 0
NYA W-10.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick glass panes, and burglar proofing | nr | 2 |  | 0
NYA W-10.5 | Mild steel top hang window overall size 600 x 450mm with 2 No. 300 x 300 mm clear opening and fixed sashes complete | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
NYA W-10.6 | Double leaf steel casement door overall size 1200 x 2100mm high complete with 4mm thick clear glass panes and burglar proofing | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA W-10.7 | 900mm x 2100mm (W x H) | nr | 3 |  | 0
Fences
NYA W-10.8 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
NYA W-10.9 | Width 4 m, double leaf complete | nr | 1 |  | 0
Building Finishes
NYA W-10.10 | Building finishes including; constructing C20 1.0x2.0m entrance ramp, 20x100mm high ceramic skirting, 1500mm high toilet walls and floor ceramic tiling, C20 concrete window cills, 700mm wide C20 concrete splash apron; Soft board notice board fixed to the wall, area 1.5 m2, complete to the specifications and as directed by the Engineer | Sum | 1 |  | 0
NYA W-10.11 | Construct in hardwood timber 3.25m x 0.7m x 0.7m high storage shelves on 4mm thick steel angle frames, 3 levels; installed in the main store, as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Plumbing and Drainage
NYA W-10.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
NYA W-10.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
NYA W-10.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
NYA W-10.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
NYA W-10.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
NYA W-10.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA W-10/1 |  |  |  | 0
| Collection, Page NYA W-10/2 |  |  |  | 0
| Collection, Page NYA W-10/3 |  |  |  | 0
| Collection, Page NYA W-10/4 |  |  |  | 0
| Collection, Page NYA W-10/5 |  |  |  | 0
| Collection, Page NYA W-10/6 |  |  |  | 0
| Collection, Page NYA W-10/7 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA ME-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA ME-1
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS DWD 77382
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Borehole Pumps
ME 1.1.1 | Electric multistage centrifigual submersible borehole pumpset with motor, capacity Q = 20.0m3/hr at a head of 216m delivering to Reservoir; complete with starter, delivery pressure gauge, pressure switch, protective controls against dry runs, and all accessories as Grundfos or equal approved | No. | 1 |  | 0
0
ME 1.1.2 | Manufacturer's recommended spares for 3 years operation of 1No. borehole pumps including 1no. spare motor for the pump | Set | 1 |  | 0
297
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Borehole Pump, Guard and Attendant Houses
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 4 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 4 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 3 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 6 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 6 |  | 0
EE 1.2 | Earthing and Lightning Protection
EE 1.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 12 |  | 0
EE 1.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 3 |  | 0
EE 1.2.3 | Test clamp complete as by FURSE or equal. | No. | 3 |  | 0
EE 1.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 3 |  | 0
EE 1.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | M | 20 |  | 0
EE 1.2.6 | 150KVA Electronic stabilizer rated at 400V, 50Hz 3 phase, input voltage +/-25%, output voltage +/-5%, complete with independent phase control, input/output isolators and bypass switch and all accessories as made by Orteo of Italy or equal approved. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 1.2.7 | Motor Control Centre for borehole incorporating main circuit breaker, starter, controls and protection for pump (HIGH/LOW pressure and dry running), under and overvoltage relay and single phasing relay, power monitor, hour, volt and Amp meters, and all accessories complete as in specifications | No. | 1 |  | 0
EE 1.2.8 | Armoured cable 4corex10mm2 PVC/SWA/PVC laid in conduits to pumps complete | m | 120 |  | 0
Power Supply to Pump House
EE 1.3 | Solar Power
EE 1.3.1 | Supply and Installation of additional mono crystalline PV Solar panels rated at 280pW 12 Volts DC, include: PV solar panel support structure for mounting solar panels; all electrical accessories; to the Engineer's approval | No. | 216 |  | 0
EE 1.4 | Extension of Hydroelectricity Grid
EE 1.4.1 | 33KV line on Creosote treated poles with a guaranteed life of at least 10years, with 3Nox100mm2 AAAC plus earth wire constructed to UMEME standards complete with insulators, stay wires and all accessories. | Km | 2.3 |  | 0
EE 1.4.2 | 100KVA, 3phase, 33KV/433V Dyn11, 50Hz oil filled outdoor, plinth mounted transformer, conservator tank with silica gel breather, Temperature gauge, off-load tap changer, explosion vent, and additional neutral for grounding, protection cage, reinforced concrete plinth, and all accessories all to comply with UMEME Standards. | No | 1 |  | 0
EE 1.4.3 | Allow a Provisional Sum for Utility connections at 33KV, metering unit and connection from UMEME supply to pump control panels | Item | 1 | 30000000 | 30000000
EE 1.4.4 | Allow for profit and overheads on above. | % |  |  | 0
EE 1.4.5 | Lockable Meter Box to UMEME approval (400x600x200mm) in 2mm MS Sheets complete with cutouts and all accessories | No. | 1 |  | 0
|  |  |  | Carried to Collection | 30000000
COLLECTION
| Collection, Page NYA ME-1/1 |  |  |  | 0
| Collection, Page NYA ME-1/2 |  |  |  | 0
| Collection, Page NYA ME-1/3 |  |  |  | 30000000
|  |  |  | Carried to Summary | 30000000

## NYA ME-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA ME-2
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS DWD 77383
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Borehole Pumps
ME 1.1.1 | Electric multistage centrifigual submersible borehole pumpset with motor, capacity Q = 10.0m3/hr at a head of 178m delivering to Reservoir; complete with starter, delivery pressure gauge, pressure switch, protective controls against dry runs, and all accessories as Grundfos or equal approved | No. | 1 |  | 0
0
ME 1.1.2 | Manufacturer's recommended spares for 3 years operation of 1No. borehole pumps including 1no. spare motor for the pump | Set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Borehole Pump, Guard and Attendant Houses
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 4 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 4 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 3 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 6 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 6 |  | 0
EE 1.2 | Earthing and Lightning Protection
EE 1.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 12 |  | 0
EE 1.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 3 |  | 0
EE 1.2.3 | Test clamp complete as by FURSE or equal. | No. | 3 |  | 0
EE 1.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 3 |  | 0
EE 1.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | M | 20 |  | 0
EE 1.2.6 | 50KVA Electronic stabilizer rated at 400V, 50Hz 3 phase, input voltage +/-25%, output voltage +/-5%, complete with independent phase control, input/output isolators and bypass switch and all accessories as made by Orteo of Italy or equal approved. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 1.2.7 | Motor Control Centre for borehole incorporating main circuit breaker, starter, controls and protection for pump (HIGH/LOW pressure and dry running), under and overvoltage relay and single phasing relay, power monitor, hour, volt and Amp meters, and all accessories complete as in specifications | No. | 1 |  | 0
EE 1.2.8 | Armoured cable 4corex10mm2 PVC/SWA/PVC laid in conduits to pumps complete | m | 100 |  | 0
Power Supply to Pump House
EE 1.3 | Solar Power
EE 1.3.1 | Supply and Installation of additional mono crystalline PV Solar panels rated at 280pW 12 Volts DC, include: PV solar panel support structure for mounting solar panels; all electrical accessories; to the Engineer's approval | No. | 81 |  | 0
EE 1.4 | Extension of Hydroelectricity Grid
EE 1.4.1 | 33KV line on Creosote treated poles with a guaranteed life of at least 10years, with 3Nox100mm2 AAAC plus earth wire constructed to UMEME standards complete with insulators, stay wires and all accessories. | Km | 0.4 |  | 0
EE 1.4.2 | 50KVA, 3phase, 33KV/433V Dyn11, 50Hz oil filled outdoor, plinth mounted transformer, conservator tank with silica gel breather, Temperature gauge, off-load tap changer, explosion vent, and additional neutral for grounding, protection cage, reinforced concrete plinth, and all accessories all to comply with UMEME Standards. | No | 1 |  | 0
EE 1.4.3 | Allow a Provisional Sum for Utility connections at 33KV, metering unit and connection from UMEME supply to pump control panels | Item | 1 | 30000000 | 30000000
EE 1.4.4 | Allow for profit and overheads on above. | % |  |  | 0
EE 1.4.5 | Lockable Meter Box to UMEME approval (400x600x200mm) in 2mm MS Sheets complete with cutouts and all accessories | No. | 1 |  | 0
|  |  |  | Carried to Collection | 30000000
COLLECTION
| Collection, Page NYA ME-2/1 |  |  |  | 0
| Collection, Page NYA ME-2/2 |  |  |  | 0
| Collection, Page NYA ME-2/3 |  |  |  | 30000000
|  |  |  | Carried to Summary | 30000000

## NYA ME-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA ME-3
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (WATER OFFICE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Water Office
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 8 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 10 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 2 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 8 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 8 |  | 0
EE 2.1 | Earthing and Lightning Protection
EE 2.1.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 30 |  | 0
EE 2.1.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 4 |  | 0
EE 2.1.3 | Test clamp complete as by FURSE or equal. | No. | 4 |  | 0
EE 2.1.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 4 |  | 0
EE 2.1.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.1.6 | 63A TPN IP65 Isolator. | No. | 2 |  | 0
EE 2.1.6 | 100A TPN IP65 Isolator. | No. | 2 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 2.2 | Power Supply to Water Office |  |  | 0
0
EE 2.2.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA ME-3/1 |  |  |  | 0
| Collection, Page NYA ME-3/2 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA ME-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA ME-4
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (CHEMICAL HOUSE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Chlorine Generation & Dosing Equipment |  |  | 0
0
ME 1.1.1 | Supply and Install DOSATRON D60S model or equivalent in line proportional chemical doser or its equivalent approved by the Engineer including all inlet, outlet, drain, venturi, overflow and interconnection connection pipes to solution tank (PVC, 1") with valves and all accessories with a minimum capacity of 10-60m3/hr | nr | 1 |  | 0
ME 1.1.2 | Manual geared vertical mixers- agitators- propeller 2 blade type, stainless steel shaft, coupling, propeller diameter 600mm, fixed to rigid steel structure complete. | nr | 1 |  | 0
ME 1.1.3 | Rigid steel structure - made of black mild steel double L- profiles; intermediate stands - hot dip galvanized & coated, complete with base plates, anchors, nuts, bolts & washers, etc | nr | 1 |  | 0
ME 1.1.4 | Manufacturer's recommended spares for 3 years operation of dosing pumps | set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Chemical House
EE 2.1 | Lighting and Small Power
EE 2.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 2 |  | 0
EE 2.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 2 |  | 0
EE 2.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 1 |  | 0
EE 2.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 1 |  | 0
EE 2.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 1 |  | 0
EE 2.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 1 |  | 0
EE 2.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 1 |  | 0
EE 2.2 | Earthing and Lightning Protection
EE 2.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 20 |  | 0
EE 2.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 1 |  | 0
EE 2.2.3 | Test clamp complete as by FURSE or equal. | No. | 1 |  | 0
EE 2.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 1 |  | 0
EE 2.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.2.6 | 63A TPN IP65 Isolator. | No. | 1 |  | 0
EE 2.2.6 | 100A TPN IP65 Isolator. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 2.3 | Power Supply to Chemical House |  |  | 0
0
EE 2.3.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA ME-4/1 |  |  |  | 0
| Collection, Page NYA ME-4/2 |  |  |  | 0
| Collection, Page NYA ME-4/3 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## NYA ME-5
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA ME-5
DESCRIPTION: TOOLS AND EQUIPMENT
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Supply of all Office, Plumbing, Mechanical, Electrical, Miscellaneous, Equipment, as detailed in SPECIFICATIONS and summarized below. Supplied Items should be to the Engineer's approval
OFFICE EQUIPMENT
OE 1.1 | Writing desk 1,560 x 780 x 750 mm (L x W x H) with closed front view and 6 lockable drawers | No. | 4 |  | 0
OE 1.2 | Executive swivel, high back tilting steel office chair with arm rests and padded seat and back in black rexine | No. | 1 |  | 0
OE 1.3 | Executive steel office chairs with padded seat and back in black rexine | No. | 3 |  | 0
OE 1.4 | Steel cabinet 1,950 x 950 x 420 mm (L x W x H) with double lockable doors, 4 shelves; colour: grey | No. | 1 |  | 0
OE 1.5 | Lockable steel filing cabinet with 4 drawers | No. | 1 |  | 0
OE 1.6 | Computer Workstation complete as specified | No. | 2 |  | 0
Intel Core i7-2500 3.30GHz, 6M Smart Cache processor
16 GB of DDR 1066 MHz SDRAM; 1TB SATA Hard Disk Drive
16X DVD +/- RW; 17” TFT “Ultra Sharp Flat Panel
Licensed Microsoft Windows 7
Licensed MS Office 2010 & Kaspersky Internet Security 2013
UPS of minimum specification 1500 VA
OE 1.7 | HP Laser Jet Printer | No. | 1 |  | 0
Printer speed- up to 24 ppm black; Processor speed- 533 MHz
Paper trays- 2 trays; Input capacity- Up to 500sheets
Memory- 544MB (512MB DDR SDRAM)
Media size- Max. A4; 10/100 Network Interface Card
5no. Replacement Toner Cartridges
Bi-directional parallel cable; USB printer cable
PLUMBING TOOLS AND EQUIPMENT
PE 2.1 | Blowlamp: pump action, pressure type, approx. 0.5 litre capacity, complete with wind proof nozzle and one set of replacement parts | No. | 2 |  | 0
PE 2.2 | Brushes, wire type for cleaning parts, 300 mm long, 3 rows of approximately15 tufts with 25 mm long steel bristles | No. | 2 |  | 0
PE 2.3 | File, flat machinist's, length 250 mm, second cut | No. | 1 |  | 0
PE 2.4 | File, flat machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.5 | File, flat machinist's, length 250 mm, bastard cut | No. | 1 |  | 0
PE 2.6 | File, half-round machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.7 | File, half-round machinist's, length 250 mm, but bastard cut | No. | 1 |  | 0
PE 2.8 | File handles, 100 x 27 mm | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
PE 2.9 | Hammer, mechanic's, 200 & tempered forged steel head, ash or white hickory handle, polished face | No. | 1 |  | 0
PE 2.10 | Precision Level, plumb and spirit, approximately 600 x 25 x 75 mm, varnished beech wood or aluminium, class of accuracy 0.025 mm/m | No. | 1 |  | 0
PE 2.11 | Mattocks | No. | 1 |  | 0
PE 2.12 | Pliers, arc joint, minimum 5 adjustments, 240 mm long | No. | 1 |  | 0
PE 2.13 | Saw, Plumbers, 400 mm, fine tooth edge for cutting metal and coarse teeth for cutting wood, complete with 5No. blades | No. | 1 |  | 0
PE 2.14 | Screw drivers, assorted, hammer-proof, non-inflammable plastic handle | Set | 1 |  | 0
PE 2.15 | Shovels | No. | 1 |  | 0
PE 2.16 | Tape measure, Stanley type steel, metric units, 5 m | No. | 1 |  | 0
PE 2.17 | Tapping machine, furnished with ratchet crank for manual operation, for making tappings from DN 15 (1/2") to DN 50 (2") on mains of DN 25 (1”) to DN 300 (12”) | No. | 1 |  | 0
PE 2.18 | Die set with stock, for threading from DN 15 to DN 150 | No. | 1 |  | 0
PE 2.19 | Vice with parallel jaw 100 mm as Peddinghaus, Matador 10203, portable type, with tripod stand | No. | 1 |  | 0
MECHANICAL TOOLS AND EQUIPMENT
ME 3.1 | 0.5 kg axe. | No. | 1 |  | 0
ME 3.2 | Caliper, precision slide type, metric unit. | No. | 1 |  | 0
ME 3.3 | Carpenter chisel from 6.4 mm to 25.4 mm bevelled edge. | Set | 1 |  | 0
ME 3.4 | Mason chisel from 25.4 mm to 50 mm wide blade. | Set | 1 |  | 0
ME 3.5 | Carpenter's screw clamps, 250 mm opening. | No. | 2 |  | 0
ME 3.6 | Carpenter's screw clamps, 500 mm opening. | No. | 2 |  | 0
ME 3.7 | Square set, metric unit. | No. | 1 |  | 0
ME 3.8 | Crowbars, small, medium, large. | Set | 1 |  | 0
ME 3.9 | Gasket cutter, 600 mm. | No. | 1 |  | 0
ME 3.10 | Dividers. | Set | 1 |  | 0
ME 3.11 | Six assorted files, half round, 250mm, including handles. | Set | 1 |  | 0
ME 3.12 | Spare file handles, 100 x 27 mm. | No. | 5 |  | 0
ME 3.13 | 3 suitable feelers, in tenths of millimetre and 150 mm long. | Set | 1 |  | 0
ME 3.14 | Mechanic's hammer, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.15 | Carpenter's claws 1/5, 1/2. 1 and 2 kg. | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
0
ME 3.16 | Sledge hammer, 3 kg. | No. | 2 |  | 0
ME 3.17 | Rubber mallet, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.18 | Hooks to remove packings. | No. | 2 |  | 0
ME 3.19 | Grease gun, 200 ml minimum. | No. | 1 |  | 0
ME 3.20 | Oiler, approx. 200 ml capacity, trigger operated, 150mm long flexible spout. | No. | 1 |  | 0
ME 3.21 | Carpenter's pincers, 200 mm jointer's shouldered type. | No. | 2 |  | 0
ME 3.22 | Adjustable pliers, 300 mm and 400mm. | Set | 1 |  | 0
ME 3.23 | Round nose pliers, 150 mm. | No. | 1 |  | 0
ME 3.24 | Puller set, inside-outside, to suit bearings and couplings incorporated in the equipment. | No. | 1 |  | 0
ME 3.25 | Punches, 1 - 10 mm. | Set | 1 |  | 0
ME 3.26 | Reamer, 7 - 17 mm. | Set | 1 |  | 0
ME 3.27 | Hack Saw, adjustable tubular frame, length 250-300mm, including 20 Nos. of spare blades. | No. | 1 |  | 0
ME 3.28 | Sockets, numbers ranging from 2 to 38, with ratchets and handles | Set | 1 |  | 0
ME 3.29 | Scraper spoon, flat and triangular type. | Set | 1 |  | 0
ME 3.30 | Snips, tin plate cutter, 300 mm. | No. | 1 |  | 0
ME 3.31 | Shears, universal, 200 mm. | No. | 1 |  | 0
ME 3.32 | Wrench, chain 16 to 100 mm capacity. | No. | 1 |  | 0
ME 3.33 | Wrench, pipe 300/400/600/900 mm. | No. | 2 |  | 0
ME 3.34 | Wrench, allen set, numbers ranging from 2 to 38. | No. | 1 |  | 0
ME 3.35 | Open ended spanner, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.36 | Ring spanners, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.37 | Hexagon nut drive spanners, 2-14 mm, metric size. | Set | 1 |  | 0
MISCELLANEOUS TOOLS
MT 5.1 | Contractor's pick axe with point and chisel steel end, length 800 mm | No. | 2 |  | 0
MT 5.2 | Steel hoe, blade width 200 mm, 1.5 kg complete with good wooden handle | No. | 2 |  | 0
MT 5.3 | Seamless pressed tray wheelbarrow, steel frame, with pneumatic wheels, 80 litres | No. | 2 |  | 0
MT 5.4 | Steel Slashers | No. | 5 |  | 0
MT 5.5 | 33CC 2-Cycle Petrol-Powered engine Straight Shaft Attachment Capable String Lawn Trimmer with 17-inch cutting path (including 10No. replacement trimmer lines) | No. | 1 |  | 0
MT 5.6 | Steel rakes | No. | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA ME-5/1 |  |  |  | 0
| Collection, Page NYA ME-5/2 |  |  |  | 0
| Collection, Page NYA ME-5/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## NYA S-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA S-1
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - BOYS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 43.4 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 75 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 187 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 12 |  | 0
|  |  |  | Carried to Collection | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA S-1.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
NYA S-1.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
NYA S-1.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
NYA S-1.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
NYA S-1.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
NYA S-1.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
NYA S-1.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
NYA S-1.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
NYA S-1.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Water and Drainage
NYA S-1.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
NYA S-1.11 | Construct Urinal facility complete with floor trap, domical removable cast iron grating, gulley trap and including OD 110 uPVC PN 6 drainage pipework to soak away pit | sum | 1 |  | 0
NYA S-1.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
NYA S-1.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
NYA S-1.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
NYA S-1.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA S-1/1 |  |  |  | 0
| Collection, Page NYA S-1/2 |  |  |  | 0
| Collection, Page NYA S-1/3 |  |  |  | 0
| Collection, Page NYA S-1/4 |  |  |  | 0
| Collection, Page NYA S-1/5 |  |  |  | 0
| Collection, Page NYA S-1/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## NYA S-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA S-2
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - GIRLS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 20.3 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
|  |  |  | Carried to Collection | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 80 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 193 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 13 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA S-2.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 6 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
NYA S-2.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
NYA S-2.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
NYA S-2.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
NYA S-2.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
NYA S-2.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
NYA S-2.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
NYA S-2.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
NYA S-2.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
NYA S-2.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
NYA S-2.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
NYA S-2.12 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm dia chromium plated pillar taps | nr | 1 |  | 0
NYA S-2.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
NYA S-2.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
NYA S-2.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
NYA S-2.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
NYA S-2.17 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page NYA S-2/1 |  |  |  | 0
| Collection, Page NYA S-2/2 |  |  |  | 0
| Collection, Page NYA S-2/3 |  |  |  | 0
| Collection, Page NYA S-2/4 |  |  |  | 0
| Collection, Page NYA S-2/5 |  |  |  | 0
| Collection, Page NYA S-2/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## NYA S-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
NYAKABALE RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. NYA S-3
DESCRIPTION: 4 STANCE PUBLIC WATERBORNE TOILETS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 110 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 37.6 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E323 | Depth 0.5 - 1 m | m³ | 37.2 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to toilet block and compacted to 98% MOD AASHTO | m³ | 5.2 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 4.2 |  | 0
E647 | 200mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 16.5 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 42 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F251 | 10mm aggregate | m³ | 8.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete for footings, grade C15 of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 2.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522 | Thickness 150-300mm | m³ | 4.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 3 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.7 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.4 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 9.6 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | kg | 150 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 28.3 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 17.7 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 47 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 21 |  | 0
|  |  |  | Carried to Collection | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 4 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 67 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.7 |  | 0
Masonry
External quality weather guard paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 49 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 79 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153.1 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 78.1 |  | 0
W153.2 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a steel float | m² | 49 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 78.1 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.3 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16.5 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 49 |  | 0
MISCELLANEOUS WORKS
Structural
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, stays, plugging and fixing to wall
NYA S-3.1 | Top hung double leaf hinged windows overall size 3450 x 1150mm high comprising of 3mm thick mild steel panes welded on a 25x25x3mm thick angle frame and epoxy coated colour blue | nr | 1 |  | 0
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
NYA S-3.2 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
NYA S-3.4 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
NYA S-3.5 | Single leaf door overall size 1000 x 2100mm high | nr | 3 |  | 0
Roofing
NYA S-3.6 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, metal lathe ceiling and eaves, and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 34.7 |  | 0
Building Finishes
NYA S-3.7 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
NYA S-3.8 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
NYA S-3.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 10no. toilet paper holders, installation of floor drains with associated pipework and fitting s connected to soak pit, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
NYA S-3.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
NYA S-3.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
NYA S-3.12 | Construct Urinal facility with perforated DN 20 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap | sum | 1 |  | 0
NYA S-3.13 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm diameter chromium plated pillar taps | sum | 1 |  | 0
NYA S-3.14 | Provide materials and construct a hand washing facility complete with wash hand basins, DN 13/20 GI/PPR plumbing pipework, uPVC drainage pipework, all fittings, gulley and bottle traps, valves, 13mm diameter chromium plated pillar taps, waste outlet gratings, all accessories, including single low level wash hand basin for disabled person's usage; as per specifications and drawings and to the Engineer's approval | nr | 2 |  | 0
NYA S-3.15 | Excavate and construct standard manholes in 200mm thick blockwork, internal depth not exceeding 1.0m, bonded in concrete mortar(1:5) and rendered internally with concrete mortar (1:4), concrete benching, complete with and including CI frame and cover, and interconnecting OD 110mm pvc drain pipes to toilet block | nr | 4 |  | 0
NYA S-3.16 | Supply and Install OD 110 mm uPVC PN 6 drainage pipework to BS 4660, complete with spigot and socket joints, all fittings; from toilet block to Septic Tank and Soak Pit | m | 78 |  | 0
NYA S-3.17 | Excavate and construct Septic Tank of effective capacity 15.4m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty cast iron manhole covers | Sum | 1 |  | 0
NYA S-3.18 | Excavate and construct 2500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
NYA S-3.19 | Supply and install squatting type low level water closet suite complete with WC pan, heavy duty cistern complete with anti-vandal cage, flush pipe, connected to nearest manhole; all to the Engineer's satisfaction | nr | 3 |  | 0
NYA S-3.20 | Supply and install seat type low level water closet suite complete with WC pan, heavy duty cistern, flush pipe complete with anti-vandal cage, connected to nearest manhole; all to the Engineer's satisfaction | nr | 2 |  | 0
NYA S-3.31 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
| Power Supply to Waterborne Toilet |  |  | 0
0
NYA S-3.32 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
Carried to Collection
COLLECTION
| Collection, Page NYA S-3/1 |  |  |  | 0
| Collection, Page NYA S-3/2 |  |  |  | 0
| Collection, Page NYA S-3/3 |  |  |  | 0
| Collection, Page NYA S-3/4 |  |  |  | 0
| Collection, Page NYA S-3/5 |  |  |  | 0
| Collection, Page NYA S-3/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 2 | 0 | 0
|  |  |  | Carried to Summary | 0

## Summary-Mutunda
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
CONSTRUCTION OF MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
Grand Summary
Bill No | Description | Investment Costs
UShs
WATER SUPPLY AND EQUIPMENT
MUT W-1 | Borehole Pump Station (DWD 77378) | 0
MUT W-2 | Borehole Pump Station (DWD 77379) | 0
MUT W-3 | Borehole Pumping Mains (DWD 77378) to Popara West Reservoir | 0
MUT W-4 | Borehole Pumping Mains (DWD 77378) to Diima Reservoir | 0
MUT W-5 | Popara Reservoir Storage Reservoir and Site Works | 0
MUT W-6 | Popara West Distribution Network | 0
MUT W-7 | Popara West Intensification Network | 0
MUT W-8 | Teyago Storage Reservoir and Site Works | 0
MUT W-9 | Teyago Distribution Network | 0
MUT W-10 | Teyago Intensification Network | 0
MUT W-11 | Chemical House (2No.) | 0
MUT W-12 | Borehole Guard / Attendant House (1No.) | 0
MUT W-13 | Water Office Block | 0
MUT ME-1 | Mechanical & Electrical Works (DWD 77378) | 30000000
MUT ME-2 | Mechanical & Electrical Works (Water Office) | 0
MUT ME-3 | Mechanical & Electrical Works (Chemical House - 2No.) | 0
MUT ME-4 | Tools and Equipment | 0
SANITATION
MUT S-1 | 5 Stance VIP Latrine (Boys) - 1No. | 0
MUT S-2 | 5 Stance VIP Latrine (Boys) - 1No. | 0
MUT S-3 | 4 Stance Waterborne Toilet - 1No. | 0
0
| Sub-Total 1 | 30000000
| Allow for 10% contingency | 3000000
| Sub-Total 2 | 33000000
| Allow for 18% VAT | 5940000
| GRAND TOTAL | 38940000

## MUT W-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-1
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77378
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 49 |  | 0
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 33.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to pump house area and compacted to 98% MOD AASHTO | m³ | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.9 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 7.9 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 213 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.9 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and generator plinth of the following thickness
F622 | Thickness 150-300mm | m³ | 38 |  | 0
Suspended Slabs
Placing reinforced concrete, grade C25, for false slab (ceiling) of the following thickness
F631 | Thickness not exceeding 150mm | m³ | 1.9 |  | 0
|  |  |  | Carried to Collection | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to floor and pump house of the following width
G214 | Width: 0.4-1.22m; to false slab soffits | m² | 38.6 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244.1 | Width: 0.4-1.22m; to floor and generator plinth | m² | 5.7 |  | 0
G244.2 | Width: 0.4-1.22m; to sides of the ring beam | m² | 4.5 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 156 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 26.5 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of Pump Stations | m2 | 40.6 |  | 0
PIPEWORK - FITTINGS AND VALVES
Pipework and Fittings for DWD 77378 with yield of 45m3/hr
Ductile spun iron/ steel pipes with spigot and socket type joints and cement mortar linings, 100 mm ND DI PN16 Pipes, all to EN 545 and including approved rubber gaskets, trench excavation, lowering, laying and jointing of pipes; not in trenches including casting in as required
All pipe specials are annotated and specified on the pump station drawing. The code indicated refers to the code on the drawing.
Bends
J311.1 | BH11 - DN 100mm x 45deg flanged small radius bend | No | 2 |  | 0
J311.2 | BH23 - DN 100mm x 90deg flanged small radius bend | No | 2 |  | 0
|  |  |  | Carried to Collection | 0
Junctions and Branches
J312.1 | BH6 - DN 100mm flanged tee with 25mm female threaded branch | No | 2 |  | 0
Adaptors
J351.1 | BH8 - DN 15mm diam. Hexagon nipple | No | 1 |  | 0
J351.2 | BH16 - DN 25mm diam. Hexagon nipple | No | 2 |  | 0
J351.3 | BH2 - DN100mm Detachable / Maxi Flanged coupling | No | 2 |  | 0
Glands
J361.1 | BH4 - DN 100mm Double-flexible rubber pipe flanged coupling | No | 2 |  | 0
Straight specials - DN 100 mm pipe with fittings
J381.1 | BH1 - plain threaded both ends, nominally 3000mm long, cut to suit on site | No | 1 |  | 0
J381.2 | BH3 - DN100 Steel/DI/uPVC/HDPE PN16 riser pipes from submersible pump to top plate; complete to match pump outlet size and pumphouse pipe work | m | 75 |  | 0
J381.3 | BH12 - flanged both ends, 800mm f/f | No | 1 |  | 0
J381.4 | BH14 - flanged both ends, 400mm f/f | No | 1 |  | 0
J381.5 | BH19 - flanged both end, nominally 1500mm, cut-to-suit on site | No | 1 |  | 0
Gate Valves
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | DN 100mm | No | 2 |  | 0
Air Valves
BH 18- Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 50 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J861.1 | DN 100mm | No | 1 |  | 0
|  |  |  | Carried to Collection | 0
Pressure Gauge
J891.1 | BH10 - WIKA pressure gauge, DN 100mm case, glycerine filled with 15mm male thread | No | 1 |  | 0
Non-Return Valves
BH 15 - Flanged Non return Valves shall confirming to BS EN 12334:2001, flanges to EN 1092, all to PN16 the follwing pipe sizes.
J861.1 | DN 100mm | No | 1 |  | 0
Bulk Flow Meter
J991.1 | BH13 - flanged DN 100mm MEINECKE Cosmos WP bulk water meter | No | 1 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Isolated pipe supports
L811 | Pipe support 1 - mass concrete 200mm x 200mm x 600mm high, Class 20/20, complete with shuttering, to pipes | nr | 1 |  | 0
L812 | Pipe support 2 - mass concrete 200mm x 200mm x nominal 500mm high, Class 20/20, complete with shuttering, to valve (BH15) and tee (BH6) | nr | 2 |  | 0
L813 | Pipe support 3 - mass concrete 500mm x300mm x nominal 500mm high, Class 20/20, complete with shuttering, to bend | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 876 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 263 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 10 |  | 0
PAVINGS
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 36 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces, as detailed in the drawings, for walls of the following thickness
U521 | 230 mm thick | m2 | 99.2 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.9 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 34.6 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 61.2 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 26.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 25.7 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 38.6 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 50.6 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 48.4 |  | 0
MISCELLANEOUS WORKS
Roofing
MUT W-1.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board and all roofing timber, eave closing, gauge 26 prepainted GCI resin sheeting and ridges | m² | 38.7 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories, including aluminium mosquito proof wire gauze welded to mild steel frames in 300mm high permanent vents
MUT W-1.2 | Single leaf steel door, size 900 x 2400mm with 700mm high 4mm thick glass panes and burglar proofing; complete | nr | 1 |  | 0
MUT W-1.3 | Double leaf door overall size 1800 x 2400mm high filled in with 20 x 2mm thick mild steel square hollow section grating welded to door, complete | nr | 1 |  | 0
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
MUT W-1.4 | Steel frame glazed window, 1200mm by 2000mm clear opening; include frame, glazing, all iron mongery | nr | 3 |  | 0
Building Finishes
MUT W-1.5 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-1/1 |  |  |  | 0
| Collection, Page MUT W-1/2 |  |  |  | 0
| Collection, Page MUT W-1/3 |  |  |  | 0
| Collection, Page MUT W-1/4 |  |  |  | 0
| Collection, Page MUT W-1/5 |  |  |  | 0
| Collection, Page MUT W-1/6 |  |  |  | 0
| Collection, Page MUT W-1/7 |  |  |  | 0
| Collection, Page MUT W-1/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-2
DESCRIPTION: BOREHOLE PUMP STATION (1No.) DWD 77379
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance | m2 | 900 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
15000
D310 | Diameter 150-500 mm | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 978 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 294 |  | 0
MISCELLANEOUS WORKS
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-2/1 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-3
DESCRIPTION: BOREHOLE PUMPING MAINS DWD 77378 TO POPARA WEST RESERVOIR
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 10848 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 7 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 4 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS EN1452, with flexible joints to BS EN14814 all to PN16, OD160mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 9040 |  | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Flanged adaptor to fit uPVC pipe spigots to BS 3505, flanges to BS 4505, all to PN16, and of the following sizes
J351.1 | 150 mm ND | nr | 10 |  | 0
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.1 | 150 mm ND | nr | 3 |  | 0
Ductile Iron all flanged 22.5 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.2 | 150 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 25 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 150 mm ND | nr | 1 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valves, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes;all to PN16
J911.1 | 150 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 1 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 1 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 4 |  | 0
|  |  |  | Carried to Collection | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.1 | Diameter not exceeding 300 mm ND | m | 24 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes | nr | 23 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 203.4 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 5 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 100 mm ND | m | 7790 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 100 mm ND | m | 1000 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 100 mm ND | m | 250 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-3/1 |  |  |  | 0
| Collection, Page MUT W-3/2 |  |  |  | 0
| Collection, Page MUT W-3/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-4
DESCRIPTION: BOREHOLE PUMPING MAINS DWD 77378 TO DIIMA RESERVOIR
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 7664 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 6 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 4 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS EN1452, with flexible joints to BS EN14814 all to PN16, OD110mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 6370 |  | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Flanged adaptor to fit uPVC pipe spigots to BS 3505, flanges to BS 4505, all to PN16, and of the following sizes
J351.1 | 100 mm ND | nr | 6 |  | 0
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.1 | 100 mm ND | nr | 3 |  | 0
Ductile Iron all flanged 22.5 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.2 | 100 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN16 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 100 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valves shall conform to BS EN 1074 : 2000 Part 4, 25 mm ND, as specified, flanges to EN 1092, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN16 as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 100 mm ND | nr | 1 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valves, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes;all to PN16
J911.1 | 100 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 1 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 1 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 3 |  | 0
|  |  |  | Carried to Collection | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.1 | Diameter not exceeding 300 mm ND | m | 16 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes | nr | 16 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 143.325 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 5 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 100 mm ND | m | 5120 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 100 mm ND | m | 1000 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 100 mm ND | m | 250 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-4/1 |  |  |  | 0
| Collection, Page MUT W-4/2 |  |  |  | 0
| Collection, Page MUT W-4/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-5
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-5
DESCRIPTION: POPARA WEST STORAGE RESERVOIR AND SITE WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for works | m2 | 625 |  | 0
EARTHWORKS
General Excavation
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 16.5 |  | 0
Excavation for foundations
Ordinary Soil
Excavation for foundations (stub columns), in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth 0.5-1m | m³ | 27 |  | 0
E324 | Depth 1-2m | m³ | 36 |  | 0
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5 - 1.0 m | m³ | 2.7 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces in the following materials
E522 | Material other than topsoil, rock or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 72 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 13.1 |  | 0
E533 | Rock | m³ | 2.7 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 13.9 |  | 0
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to foundations and compacted to 98% MOD AASHTO | m³ | 2.7 |  | 0
Filling Ancillaries
Trimming of Filled Surfaces
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 72 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 425 |  | 0
Provision of Hardcore
E810 | Provision and placement of 300mm thick hardcore base for the tank footings | m² | 27 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F131 | 10 mm aggregate | m³ | 1.4 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F151 | 10 mm aggregate | m³ | 13.1 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, grade C15, of the following thickness
F512 | Thickness 150-300mm | m³ | 1.4 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete, grade C25, for column base footings of the following thickness
F522 | Thickness 300-500 mm | m³ | 10.8 |  | 0
Columns
Placing reinforced concrete, grade C25, for columns of the following thickness
F522 | Thickness 300-500 mm | m³ | 2.3 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G245 | Width exceeding 1.22m | m² | 51.8 |  | 0
Reinforcement
High Yield Steel
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 1634 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G812 | With steel float finish | m² | 23 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK - PIPES
Plastic Drain Pipes
uPVC drain pipes, conforming to BS EN1452, ith flexible joints to BS EN14814, 160 mm OD PN 6, laid in trench to the following depths
I512 | Depth not exceeding 1.5m | m | 30 |  | 0
PIPEWORK - FITTINGS AND VALVES
Cast or Spun Iron Pipe Fittings
external epoxy coated to AWWA C213
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.1 | 50 mm ND | nr | 1 |  | 0
J311.2 | 80 mm ND | nr | 2 |  | 0
J311.3 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.4 | 150 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.5 | 50 mm ND | nr | 1 |  | 0
J311.6 | 80 mm ND | nr | 2 |  | 0
J311.7 | 150 mm ND | nr | 2 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.8 | 150 mm ND | nr | 1 |  | 0
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 150/80 mm ND | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Double Collars
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J341.1 | 50 mm ND | nr | 1 |  | 0
J341.2 | 80 mm ND | nr | 1 |  | 0
J341.3 | 150 mm ND | nr | 1 |  | 0
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 16, and of the following sizes
J341.5 | 150 mm ND | nr | 1 |  | 0
Adaptors
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 2 |  | 0
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.2 | OD 90 mm X 3" | nr | 1 |  | 0
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN16, and of the following sizes
J351.1 | 150 mm ND | nr | 1 |  | 0
Bellmouths
Flanged bellmouth to ISO 2531, flanges to ISO 2441, of the following sizes all to PN 10
J372.1 | 150 mm ND | nr | 1 |  | 0
Straight Specials
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 10 and of the following sizes
J381.1 | 50 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.2 | 50 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.3 | 50 mm ND not exceeding 3.0m | nr | 1 |  | 0
J381.4 | 50 mm ND not exceeding 6.0m | nr | 3 |  | 0
J381.5 | 80 mm ND not exceeding 0.6m | nr | 4 |  | 0
J381.6 | 80 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.7 | 80 mm ND not exceeding 3.0m | nr | 1 |  | 0
J381.8 | 80 mm ND not exceeding 6.0m | nr | 3 |  | 0
J381.9 | 150 mm ND not exceeding 0.6m | nr | 4 |  | 0
J381.10 | 150 mm ND not exceeding 1.0m | nr | 2 |  | 0
J381.11 | 150 mm ND not exceeding 3.0m | nr | 4 |  | 0
J381.12 | 150 mm ND not exceeding 6.0m | nr | 6 |  | 0
|  |  |  | Carried to Collection | 0
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 16 and of the following sizes
J381.13 | 150 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.14 | 150 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.15 | 150 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.16 | 150 mm ND not exceeding 6.0m | nr | 3 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491.1 | 80 mm ND | nr | 1 |  | 0
J491.2 | 150 mm ND | nr | 1 |  | 0
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 80 mm ND | nr | 2 |  | 0
J811.2 | 150 mm ND | nr | 1 |  | 0
Ball Float Valves
Flanged Balanced ball float valve, flanges to BS 4505, all to PN16
J891.1 | 150 mm ND | nr | 1 |  | 0
Bulk Flow Meter
"Woltman" Helix Type Bulk Flow Meter inclusive of all couplings, adaptors, steel pipe distance pieces, CI valves, thrust blocks, etc and all other fittings to make the installation complete, as specified, all fittings to PN 10, including lockable vented blockwork chamber with cast in valve surface boxes, and on the following main pipe sizes
J991.1 | 80 mm ND | nr | 1 |  | 0
J991.2 | 150 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Manholes
Blockwork Manhole
Blockwork chamber complete with C20 concrete base, vented lockable manhole cover, valve surface boxes, galvanised step irons, as specified in the drawings, and of the following depths
K171 | Depth not exceeding 1.5m | nr | 4 |  | 0
|  |  |  | Carried to Collection | 0
Other Chambers
In situ Concrete Chambers
Washout out fall structure, complete including flap valve, all fittings and pipework necessary to complete installation, as specified in drawings, and of the following depths; all fittings and pipework to PN 10
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Supply and construct grouted stone pitching using mortar mix 1:4, include 50mm thick coping using 1:2:4 concrete mix on top of the stone pitching of same width as the wall thickness for drains of cross section
K 491 | Cross section area 0.5-1.0m2 | m | 20 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 1 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for bulk meters | nr | 1 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 300 mm ND | m | 20 |  | 0
MISCELLANEOUS WORKS
Supply and Install cold pressed galvanised steel sectional tank with external flanges and pitched cover with 1No. 1m wide access man way, 20m high tower, water level indicator (scale in cubic metres) and plates with inlet, outlet, washout and overflow connection complete with access points, ventilators (4 nr), walkway, handrailing, and internal and external access ladders with safety hoops, inclusive of painting, finishes and all necessary accessories to installation complete as specified and detailed in the drawings; to the Engineer's satisfaction. All tank accessories shall be of hot dipped galvanised steel.
MUT W-5.1 | Reservoir: 150m3 nominal capacity erected on a 15m high tower | nr | 1 |  | 0
MUT W-5.2 | Supply and Installation of a 15m high steel tower | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 252 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 76 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-5/1 |  |  |  | 0
| Collection, Page MUT W-5/2 |  |  |  | 0
| Collection, Page MUT W-5/3 |  |  |  | 0
| Collection, Page MUT W-5/4 |  |  |  | 0
| Collection, Page MUT W-5/5 |  |  |  | 0
| Collection, Page MUT W-5/6 |  |  |  | 0
| Collection, Page MUT W-5/7 |  |  |  | 0
| Collection, Page MUT W-5/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-6
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-6
DESCRIPTION: POPARA WEST DISTRIBUTION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 25394 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 7 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 5 |  | 0
D320 | Diameter 500 mm -1 m | nr | 3 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to all to PN10, OD160mm, laid in trench to the following depths
I512.1 | Depth not exceeding 1.5m | m | 6972 |  | 0
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to BS4346 all to PN10, OD110mm, laid in trench to the following depths
I512.2 | Depth not exceeding 1.5m | m | 1655 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 90mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 6463 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 75mm, laid in trench to the following depths
I712.2 | Depth not exceeding 1.5m | m | 1400 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 63mm, laid in trench to the following depths
I712.3 | Depth not exceeding 1.5m | m | 825 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 50mm, laid in trench to the following depths
I712.4 | Depth not exceeding 1.5m | m | 3848 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 150/150 mm ND | nr | 1 |  | 0
J321.2 | 150/65 mm ND | nr | 1 |  | 0
J321.3 | 150/50 mm ND | nr | 1 |  | 0
J321.4 | 100/100 mm ND | nr | 1 |  | 0
J321.5 | 80/65 mm ND | nr | 1 |  | 0
J321.6 | 65/40 mm ND | nr | 1 |  | 0
Tapers
Ductile iron all flanged concentric taper to EN 545, flanges to EN 1092-2 all to PN10, cement mortar lined, and of the following sizes
J331.1 | 150/100 mm ND | nr | 1 |  | 0
J331.2 | 150/50 mm ND | nr | 1 |  | 0
J331.3 | 100/80 mm ND | nr | 1 |  | 0
J331.4 | 100/50 mm ND | nr | 1 |  | 0
J331.5 | 65/40 mm ND | nr | 2 |  | 0
J331.6 | 50/40 mm ND | nr | 3 |  | 0
Adaptors
Flanged adaptor to fit uPVC pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 150 mm ND | nr | 5 |  | 0
J351.2 | 100 mm ND | nr | 4 |  | 0
Plastic Pipe Fittings
Bends
uPVC 22.5 degree bends with push-fit joint for use with uPVC pipes, to EN 1401, all to PN 10, and of the following sizes
J311.1 | 150mm ND | nr | 2 |  | 0
Adaptors
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.1 | OD 90 mm X 3" | nr | 3 |  | 0
J651.2 | OD 75 mm X 2 1/2" | nr | 2 |  | 0
J651.3 | OD 63 mm X 2" | nr | 2 |  | 0
J651.4 | OD 50 mm X 1 1/2" | nr | 6 |  | 0
|  |  |  | Carried to Collection | 0
End caps
Compression HDPE end caps to fit uPVC spigots, to EN 12201 and to PN 10 of the following spigot sizes
J691.1 | ND 80 mm | nr | 1 |  | 0
J691.2 | ND 40 mm | nr | 6 |  | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 4 |  | 0
J811.2 | 100 mm ND | nr | 2 |  | 0
J811.3 | 80 mm ND | nr | 1 |  | 0
J811.4 | 65 mm ND | nr | 2 |  | 0
J811.5 | 50 mm ND | nr | 1 |  | 0
J811.6 | 40 mm ND | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 25 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN10, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 150 mm ND | nr | 1 |  | 0
J862.2 | 65 mm ND | nr | 1 |  | 0
Washouts
Type 1 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 150 mm ND | nr | 1 |  | 0
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 80 mm ND | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 3 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 11 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 6 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 48 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 11 |  | 0
K820.2 | Marker posts for air valves | nr | 2 |  | 0
K820.3 | Marker posts for wash outs | nr | 3 |  | 0
K820.4 | Marker posts for pipes | nr | 53 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 476.1675 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 2 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 19163 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-6/1 |  |  |  | 0
| Collection, Page MUT W-6/2 |  |  |  | 0
| Collection, Page MUT W-6/3 |  |  |  | 0
| Collection, Page MUT W-6/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-7
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-7
DESCRIPTION: POPARA WEST INTENSIFICATION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | m2 | 10800 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
D320 | Diameter 500 mm -1 m | nr | 2 |  | 0
PIPEWORK-PIPES
Plastic Pressure Pipes- Distribution
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 40 mm, laid in trench to the following depths
I711.1 | Depth not exceeding 1.5m | m | 3000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 32 mm, laid in trench to the following depths
I711.2 | Depth not exceeding 1.5m | m | 3000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 25 mm, laid in trench to the following depths
I711.3 | Depth not exceeding 1.5m | m | 3000 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD32 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 1 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
Make a connection for OD25 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 1 |  | 0
J791.2 | OD 75 mm | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 5 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
K731 | Not exceeding 300 mm ND | m | 56 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 202.5 |  | 0
|  |  |  | Carried to Collection | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 7000 |  | 0
Pipe surrounds, of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds, of mass concrete , for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
Consumer Connections
Make DN20 consumer connection to the distribution main (maximum 100m), complete, inclusive of excavation, backfill, saddle clamp, ferrule, taps,domestic water meter and all fittings for connection to GI or HDPE service pipes, as detailed in the drawings, for the following mains sizes and all to PN10
J891.1 | ND 40 mm | nr | 80 |  | 0
J891.2 | ND 50 mm | nr | 80 |  | 0
J891.3 | ND 65 mm | nr | 80 |  | 0
J891.4 | ND 100 mm | nr | 80 |  | 0
J891.5 | ND 150 mm | nr | 80 |  | 0
Public Stand Posts
Construct a double faucet Stand Post complete as in drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fitings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN 10 (service line measured separately under items I712)
L999.1 | ND 20 mm (3/4") | nr | 10 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-7/1 |  |  |  | 0
| Collection, Page MUT W-7/2 |  |  |  | 0
| Collection, Page MUT W-7/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## MUT W-8
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-8
DESCRIPTION: TEYAGO STORAGE RESERVOIR AND SITE WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for works | m2 | 625 |  | 0
EARTHWORKS
General Excavation
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 3.7 |  | 0
Excavation for foundations
Ordinary Soil
Excavation for foundations (stub columns), in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth 0.5-1m | m³ | 13.5 |  | 0
E324 | Depth 1-2m | m³ | 6.8 |  | 0
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5 - 1.0 m | m³ | 1 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces in the following materials
E522 | Material other than topsoil, rock or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 18 |  | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 6.6 |  | 0
E533 | Rock | m³ | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 7 |  | 0
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to foundations and compacted to 98% MOD AASHTO | m³ | 1 |  | 0
Filling Ancillaries
Trimming of Filled Surfaces
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 36 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 18 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 425 |  | 0
Provision of Hardcore
E810 | Provision and placement of 300mm thick hardcore base for the tank footings | m² | 13.5 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F131 | 10 mm aggregate | m³ | 0.7 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F151 | 10 mm aggregate | m³ | 6.6 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, grade C15, of the following thickness
F512 | Thickness 150-300mm | m³ | 0.7 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete, grade C25, for column base footings of the following thickness
F522 | Thickness 300-500 mm | m³ | 5.4 |  | 0
Columns
Placing reinforced concrete, grade C25, for columns of the following thickness
F522 | Thickness 300-500 mm | m³ | 1.2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G245 | Width exceeding 1.22m | m² | 25.9 |  | 0
Reinforcement
High Yield Steel
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 817 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G812 | With steel float finish | m² | 11.5 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK - PIPES
Plastic Drain Pipes
HDPE drain pipes, conforming to ISO 4427, with flexible joints, 90 mm OD PN 6, laid in trench to the following depths
I512 | Depth not exceeding 1.5m | m | 30 |  | 0
PIPEWORK - FITTINGS AND VALVES
Cast or Spun Iron Pipe Fittings
external epoxy coated to AWWA C213
Bends
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.1 | 50 mm ND | nr | 1 |  | 0
J311.2 | 80 mm ND | nr | 1 |  | 0
J311.3 | 100 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.4 | 80 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN10, cement mortar lines and of the following sizes
J311.5 | 80 mm ND | nr | 1 |  | 0
J311.6 | 100 mm ND | nr | 1 |  | 0
Ductile Iron all flanged 90 degrees duckfoot bends to EN 545, flanges to EN 1092, all to PN16, cement mortar lines and of the following sizes
J311.7 | 80 mm ND | nr | 1 |  | 0
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 80/50 mm ND | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Double Collars
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J341.1 | 80 mm ND | nr | 1 |  | 0
J341.2 | 100 mm ND | nr | 1 |  | 0
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 16, and of the following sizes
J341.3 | 80 mm ND | nr | 1 |  | 0
Adaptors
Flange adaptor of large tolerance, maxi type to fit all pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 100 mm ND | nr | 2 |  | 0
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.1 | OD 90 mm X 3" | nr | 1 |  | 0
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN16, and of the following spigot sizes
J651.1 | OD 90 mm X 3" | nr | 1 |  | 0
Bellmouths
Flanged bellmouth to ISO 2531, flanges to ISO 2441, of the following sizes all to PN 10
J372.1 | 80 mm ND | nr | 1 |  | 0
Straight Specials
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 10 and of the following sizes
J381.1 | 50 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.2 | 50 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.3 | 80 mm ND not exceeding 0.6m | nr | 4 |  | 0
J381.4 | 80 mm ND not exceeding 1.0m | nr | 2 |  | 0
J381.5 | 80 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.6 | 80 mm ND not exceeding 6.0m | nr | 4 |  | 0
J381.7 | 150 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.8 | 150 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.9 | 150 mm ND not exceeding 3.0m | nr | 1 |  | 0
J381.10 | 150 mm ND not exceeding 6.0m | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Ductile iron double flanged pipe, to EN545, flanges to BS 1092-2, cement mortar lined, all to PN 16 and of the following sizes
J381.11 | 80 mm ND not exceeding 0.6m | nr | 2 |  | 0
J381.12 | 80 mm ND not exceeding 1.0m | nr | 1 |  | 0
J381.13 | 80 mm ND not exceeding 3.0m | nr | 2 |  | 0
J381.14 | 80 mm ND not exceeding 6.0m | nr | 2 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491.1 | 150 mm ND | nr | 1 |  | 0
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 150 mm ND | nr | 1 |  | 0
Ball Float Valves
Flanged Balanced ball float valve, flanges to BS 4505, all to PN16
J891.1 | 150 mm ND | nr | 1 |  | 0
Bulk Flow Meter
"Woltman" Helix Type Bulk Flow Meter inclusive of all couplings, adaptors, steel pipe distance pieces, CI valves, thrust blocks, etc and all other fittings to make the installation complete, as specified, all fittings to PN 10, including lockable vented blockwork chamber with cast in valve surface boxes, and on the following main pipe sizes
J991.1 | 150 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
Manholes
Blockwork Manhole
Blockwork chamber complete with C20 concrete base, vented lockable manhole cover, valve surface boxes, galvanised step irons, as specified in the drawings, and of the following depths
K171 | Depth not exceeding 1.5m | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Other Chambers
In situ Concrete Chambers
Washout out fall structure, complete including flap valve, all fittings and pipework necessary to complete installation, as specified in drawings, and of the following depths; all fittings and pipework to PN 10
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Supply and construct grouted stone pitching using mortar mix 1:4, include 50mm thick coping using 1:2:4 concrete mix on top of the stone pitching of same width as the wall thickness for drains of cross section
K 491 | Cross section area 0.5-1.0m2 | m | 20 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 1 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 1 |  | 0
K820.2 | Marker posts for bulk meters | nr | 1 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 300 mm ND | m | 20 |  | 0
MISCELLANEOUS WORKS
Supply and Install cold pressed galvanised steel sectional tank with external flanges and pitched cover with 1No. 1m wide access man way, 15m high tower, water level indicator (scale in cubic metres) and plates with inlet, outlet, washout and overflow connection complete with access points, ventilators (4 nr), walkway, handrailing, and internal and external access ladders with safety hoops, inclusive of painting, finishes and all necessary accessories to installation complete as specified and detailed in the drawings; to the Engineer's satisfaction. All tank accessories shall be of hot dipped galvanised steel.
MUT W-8.1 | Reservoir: 100m3 nominal capacity erected on a 15m high tower | nr | 1 |  | 0
MUT W-8.2 | Supply and Installation of a 15m high steel tower | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
ROADS AND PAVINGS
General Site Clearance
D110 | General site clearance clearance of access road to the site | m2 | 534 |  | 0
Road Base and wearing course
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 161 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-8/1 |  |  |  | 0
| Collection, Page MUT W-8/2 |  |  |  | 0
| Collection, Page MUT W-8/3 |  |  |  | 0
| Collection, Page MUT W-8/4 |  |  |  | 0
| Collection, Page MUT W-8/5 |  |  |  | 0
| Collection, Page MUT W-8/6 |  |  |  | 0
| Collection, Page MUT W-8/7 |  |  |  | 0
| Collection, Page MUT W-8/8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-9
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-9
DESCRIPTION: TEYAGO DISTRIBUTION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | m2 | 9788 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 4 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 3 |  | 0
D320 | Diameter 500 mm -1 m | nr | 3 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes conforming to ISO 1452-2, with flexible joints to BS4346 all to PN10, OD110mm, laid in trench to the following depths
I512.1 | Depth not exceeding 1.5m | m | 15 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 75mm, laid in trench to the following depths
I712.1 | Depth not exceeding 1.5m | m | 1105 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 63mm, laid in trench to the following depths
I712.2 | Depth not exceeding 1.5m | m | 2856 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 50mm, laid in trench to the following depths
I712.3 | Depth not exceeding 1.5m | m | 4181 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Cast / Spun Iron or Steel Pipe Fittings external epoxy coated to AWWA C213
Junctions and Branches
Ductile iron all flanged tee to EN 545, flanges to EN 1092-2, all to PN10 and of the following sizes
J321.1 | 100/65 mm ND | nr | 1 |  | 0
J321.2 | 50/40 mm ND | nr | 2 |  | 0
J321.3 | 50/40 mm ND | nr | 2 |  | 0
Tapers
Ductile iron all flanged concentric taper to EN 545, flanges to EN 1092-2 all to PN10, cement mortar lined, and of the following sizes
J331.1 | 100/50 mm ND | nr | 1 |  | 0
J331.2 | 65/40 mm ND | nr | 2 |  | 0
Adaptors
Flanged adaptor to fit uPVC pipe spigots to ISO 1452, flanges to EN 1092, all to PN10, and of the following sizes
J351.1 | 100 mm ND | nr | 1 |  | 0
Plastic Pipe Fittings
Adaptors
Compression Flange adaptor to fit HDPE pipe spigots, to EN12201, all to PN10, and of the following spigot sizes
J651.1 | OD 75 mm X 2 1/2" | nr | 4 |  | 0
J651.2 | OD 63 mm X 2" | nr | 5 |  | 0
J651.3 | OD 50 mm X 1 1/2" | nr | 9 |  | 0
End caps
Compression HDPE end caps to fit uPVC spigots, to EN 12201 and to PN 10 of the following spigot sizes
J691.1 | ND 50 mm | nr | 1 |  | 0
J691.2 | ND 40 mm | nr | 5 |  | 0
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged Ductile Iron Butterfly valves to BS EN 593 : 2004 for potable water, flanges to BS 1092-2, all to PN10 for operation by hand wheel, for the following sizes; include the supply of hand wheel and chamber construction
J811.1 | 100 mm ND | nr | 1 |  | 0
J811.2 | 65 mm ND | nr | 1 |  | 0
J811.3 | 50 mm ND | nr | 2 |  | 0
J811.4 | 40 mm ND | nr | 6 |  | 0
Washouts
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN10
J911.1 | 50 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 11 |  | 0
Crossings
Open Channels
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 6 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 48 |  | 0
|  |  |  | Carried to Collection | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 11 |  | 0
K820.2 | Marker posts for air valves | nr | 2 |  | 0
K820.3 | Marker posts for wash outs | nr | 3 |  | 0
K820.4 | Marker posts for pipes | nr | 53 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 183.5325 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 2 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 6157 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-9/1 |  |  |  | 0
| Collection, Page MUT W-9/2 |  |  |  | 0
| Collection, Page MUT W-9/3 |  |  |  | 0
| Collection, Page MUT W-9/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT W-10
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-10
DESCRIPTION: TEYAGO INTENSIFICATION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | m2 | 7200 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 3 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
D320 | Diameter 500 mm -1 m | nr | 1 |  | 0
PIPEWORK-PIPES
Plastic Pressure Pipes- Distribution
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 40 mm, laid in trench to the following depths
I711.1 | Depth not exceeding 1.5m | m | 2000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 32 mm, laid in trench to the following depths
I711.2 | Depth not exceeding 1.5m | m | 2000 |  | 0
HDPE pressure pipes conforming to ISO 4427, include unions / sockets, all to PN 10, OD 25 mm, laid in trench to the following depths
I711.3 | Depth not exceeding 1.5m | m | 2000 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD32 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 1 |  | 0
J791.2 | OD 75 mm | nr | 1 |  | 0
Make a connection for OD25 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN10
J791.1 | OD 110 mm | nr | 1 |  | 0
J791.2 | OD 75 mm | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 5 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
K731 | Not exceeding 300 mm ND | m | 48 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 135 |  | 0
|  |  |  | Carried to Collection | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 4000 |  | 0
Pipe surrounds, of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 1500 |  | 0
Pipe surrounds, of mass concrete , for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
Consumer Connections
Make DN20 consumer connection to the distribution main (maximum 100m), complete, inclusive of excavation, backfill, saddle clamp, ferrule, and all fittings for connection to GI or HDPE service pipes, as detailed in the drawings, for the following mains sizes and all to PN10
J891.1 | ND 40 mm | nr | 40 |  | 0
J891.2 | ND 50 mm | nr | 40 |  | 0
J891.3 | ND 65 mm | nr | 40 |  | 0
J891.4 | ND 100 mm | nr | 40 |  | 0
J891.5 | ND 150 mm | nr | 40 |  | 0
Public Stand Posts
Construct a double faucet Stand Post complete as in drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fitings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN 10 (service line measured separately under items I712)
L999.1 | ND 20 mm (3/4") | nr | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-10/1 |  |  |  | 0
| Collection, Page MUT W-10/2 |  |  |  | 0
| Collection, Page MUT W-10/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## MUT W-11
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-11
DESCRIPTION: CHEMICAL HOUSE (2No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5 - 1.0 m | m³ | 26.7 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 0.8 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 25.4 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 2.4 |  | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 15.6 |  | 0
E533 | Rock | m³ | 0.8 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling Ancillaries
Filling
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated granular material other than topsoil, rock or artificial hard material compacted to 98% MOD AASHTO | m³ | 11.1 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.1 |  | 0
|  |  |  | Carried to Collection | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 6.3 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 40.1 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 3.8 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.3 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 4.35 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.3 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C25, for floor slab, stairs and tank base of the following thickness
F622 | Thickness 150-300mm | m³ | 3.3 |  | 0
Beams
Placing reinforced concrete grade C25, for ring beam of the following cross-sectional area
F562 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.05 |  | 0
|  |  |  | Carried to Collection | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G212 | Width: 0.1-0.2m | m² | 5.1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G243 | Width: 0.2-0.4m | m² | 20 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS 4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 304 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 22.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 22.5 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U523 | 200 mm thick | m² | 90 |  | 0
Permanent Vents
Construct dense concrete pre-cast louvered blockwork vents to BS 7263, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U590.1 | 1500mm x 1200mm (W x H) | nr | 1 |  | 0
U590.2 | 2600mm x 1200mm (W x H) | nr | 3 |  | 0
|  |  |  | Carried to Collection | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7.7 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 12.6 |  | 0
Emulsion Paint
Masonry
Internal quality emulsion paint, two coats, to the following smooth masonry surfaces, include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 71 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 22.5 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 230 mm thick | m | 22.2 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 20.7 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 44 |  | 0
|  |  |  | Carried to Collection | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 44 |  | 0
MISCELLANEOUS WORKS
Doors
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT W-11.1 | 900mm x 2400mm (W x H including 300mm wood pvo) | nr | 2 |  | 0
Roofing
MUT W-11.2 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI resin sheeting and ridges; the GCI sheet should be resin bonded or with other protection against corrosion by Chlorine | m² | 35 |  | 0
MUT W-11.3 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 20.7 |  | 0
Building Finishes
MUT W-11.4 | Chemical house finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 600mm wide C20 concrete splash apron, 2 no. drainage manholes of internal dimension 700x700mm with OD 110 PVC drainage pipework to soak pit included, 300mm x 1380mm x 100mm thick reinforced concrete doser plinth cover slabs over inlet pipe channel, etc complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
MUT W-11.5 | Supply, lay and fix inlet pipes, valves and fittings; including ball valves and flowmeter; from the outlet pipe of the nearby reservoir tank to the water tank of size OD32mm, all pipe and fittings in HDPE/uPVC/PPR to PN 10 as approved by the Engineer | Sum | 1 |  | 0
MUT W-11.6 | Supply, lay and fix drain pipes, valves and fittings from the tanks to the nearest manhole, as in the drawings, of size OD63mm, all pipe and fittings in HDPE/uPVC/PPR to PN10 as approved by the Engineer; include manhole connection and making good joint | Sum | 1 |  | 0
Mixing Tanks
MUT W-11.7 | Supply and install chlorine generation and dosing PVC tanks of 750 litres capacity as specified and as approved by the Engineer; include complete connection to Electrolytic Disinfecting Machine, Dosing equipment, and incoming DN150mm uPVC pumping Main | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-11/1 |  |  |  | 0
| Collection, Page MUT W-11/2 |  |  |  | 0
| Collection, Page MUT W-11/3 |  |  |  | 0
| Collection, Page MUT W-11/4 |  |  |  | 0
| Collection, Page MUT W-11/5 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 2 | 0 | 0
|  |  |  | Carried to Summary | 0

## MUT W-12
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-12
DESCRIPTION: GUARD AND PUMP ATTENDANT HOUSE (1No.)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
EARTHWORKS
Excavation for foundations
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 38.8 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to building area and compacted to 98% MOD AASHTO | m³ | 5.45 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 0.79 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 4.75 |  | 0
|  |  |  | Carried to Collection | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 2.25 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 3.36 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 2.25 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and steps of the following thickness
F622 | Thickness 150-300mm | m³ | 2.85 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.51 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width: 0.4-1.22m | m² | 1 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width: 0.4-1.22m; to sides of the ring beam | m² | 11.6 |  | 0
|  |  |  | Carried to Collection | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 186 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 16 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor | m2 | 16 |  | 0
BRICKWORK, BLOCKWORK, AND MASONRY
Dense Concrete Blockwork
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U521.1 | 150 mm thick | m2 | 42.2 |  | 0
U521.2 | 230 mm thick | m² | 33.1 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.4 |  | 0
Masonry
External quality weather guard paint two coats, to the following smooth concrete surfaces; include surface preparation as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 4.5 |  | 0
|  |  |  | Carried to Collection | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 46 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 21 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.2 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 39.3 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 53.7 |  | 0
MISCELLANEOUS WORKS
Roofing
MUT W-12.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes to the Engineer's satisfaction. | m2 | 15 |  | 0
MUT W-12.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600x600mm hardwood access trap door | m² | 14 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
MUT W-12.3 | Mild steel window overall size 1000 x 1100mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
MUT W-12.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
MUT W-12.5 | Single leaf solid steel door, size 900 x 2100mm; complete | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT W-12.6 | 800mm x 2100mm (W x H) | nr | 2 |  | 0
Building Finishes
MUT W-12.7 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
MUT W-12.8 | Supply and install a 1500 litre (1.5m3) Polyethylene tank as Polytank, elevated up to 1.0m above ground level on a rendered brickwork platform, complete with a DN 15mm Brass outlet tap, inlet DN 80 uPVC pipe work from overhead rain water gutters, DN 80 uPVC overflow and drainage pipework to soak pit (inclusive) as per drawings | Sum | 1 |  | 0
MUT W-12.9 | Provide and fix urine diverting squat pans as directed by Engineer | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Plumbing and Drainage
MUT W-12.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
MUT W-12.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
MUT W-12.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
MUT W-12.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
MUT W-12.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
MUT W-12.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-12/1 |  |  |  | 0
| Collection, Page MUT W-12/2 |  |  |  | 0
| Collection, Page MUT W-12/3 |  |  |  | 0
| Collection, Page MUT W-12/4 |  |  |  | 0
| Collection, Page MUT W-12/5 |  |  |  | 0
| Collection, Page MUT W-12/6 |  |  |  | 0
| Cost for 1No. Attendant House |  |  |  | 0
| Total Cost of Attendant Houses | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## MUT W-13
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT W-13
DESCRIPTION: WATER OFFICE BLOCK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for office premises | ha | 0.1 |  | 0
Trees
Cut and dispose of trees of the following girths; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
EARTHWORKS
Excavation for foundations
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E323 | Depth 0.5-1m | m³ | 52 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 1 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
|  |  | 67 |  | 0
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
|  |  | 1.5 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² |  |  | 0
|  |  |  | Carried to Collection | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 18 |  | 0
E533 | Rock | m³ | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to office area and compacted to 98% MOD AASHTO | m³ | 26 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.7 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 10 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 24 |  | 0
Trimming of surfaces filled with rock, for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 4 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 600 |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.2 |  | 0
|  |  |  | Carried to Collection | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 21 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 3.2 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab of the following thickness
F622 | Thickness 150-300mm | m³ | 17.9 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 3 |  | 0
Columns and Piers
Placing reinforced concrete, grade C25, for columns of the following cross-sectional area
F652 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.12 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to office block of the following width
G213 | Width 0.2 - 0.4m | m² | 7 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G241 | Width not exceeding 0.15m | m² | 6 |  | 0
G243 | Width 0.2 - 0.4m | m² | 33 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 577 |  | 0
|  |  |  | Carried to Collection | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 98 |  | 0
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of office block | m2 | 98 |  | 0
ROADS AND PAVINGS
Provide, transport up to site, spread, shape, and compact to atleast 95% MDD AASHTO lime stabilised gravel material for flexible road base, of the following thickness
R117 | Depth 150-300 mm applied to access road and parking area | m3 | 200 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 30 |  | 0
R712 | To a radius not exceeding 12 m | m | 30 |  | 0
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 48 |  | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U211 | 100 mm thick; Facing Bricks | m2 | 60 |  | 0
U521.1 | 150 mm thick | m2 | 12 |  | 0
U521.2 | 230 mm thick | m2 | 164 |  | 0
Permanent Vents
Dense brickwork vents to BS 7263, jointed with ordinary 1:5 cement mortar above door and window openings, including mosquito mesh, for walls of the following thickness
U589 | 150 - 230 mm thick | m2 | 3 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 8 |  | 0
|  |  |  | Carried to Collection | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 40 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 192 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 60.7 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified.
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 98 |  | 0
MISCELLANEOUS WORKS
Roofing
MUT W-13.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes connected to 3000m3 rain water polytank placed on 1m high masonry platform & complete with the necessary piping to the Engineer's satisfaction. | m2 | 136.8 |  | 0
MUT W-13.2 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 136.8 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
MUT W-13.3 | Mild steel window overall size 1500 x 1200mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 4 |  | 0
MUT W-13.4 | Mild steel window overall size 600 x 600mm high complete with 4mm thick glass panes, and burglar proofing | nr | 2 |  | 0
MUT W-13.5 | Mild steel top hang window overall size 600 x 450mm with 2 No. 300 x 300 mm clear opening and fixed sashes complete | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
MUT W-13.6 | Double leaf steel casement door overall size 1200 x 2100mm high complete with 4mm thick clear glass panes and burglar proofing | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT W-13.7 | 900mm x 2100mm (W x H) | nr | 3 |  | 0
Fences
MUT W-13.8 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 120 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
MUT W-13.9 | Width 4 m, double leaf complete | nr | 1 |  | 0
Building Finishes
MUT W-13.10 | Building finishes including; constructing C20 1.0x2.0m entrance ramp, 20x100mm high ceramic skirting, 1500mm high toilet walls and floor ceramic tiling, C20 concrete window cills, 700mm wide C20 concrete splash apron; Soft board notice board fixed to the wall, area 1.5 m2, complete to the specifications and as directed by the Engineer | Sum | 1 |  | 0
MUT W-13.11 | Construct in hardwood timber 3.25m x 0.7m x 0.7m high storage shelves on 4mm thick steel angle frames, 3 levels; installed in the main store, as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Plumbing and Drainage
MUT W-13.12 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 10; include processing water connection account with relevant water authority | Sum | 1 |  | 0
MUT W-13.13 | Supply and erect a 1000 litre (1.0m3) Polyethylene tank as Polytank, elevated up to 4m above ground level on galvanised mild steel 80mm steel sectional painted tower, complete with access ladder and platform, including C25 reinforced concrete footings, all PN 10 water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve, and pipework connection to internal office water system complete | Sum | 1 |  | 0
MUT W-13.14 | Supply and install all sanitary appliances for 1no seat type water borne closet toilet; drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres low level vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basin with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; 1 no. shower tray with all accessories; toilet paper holder, wall mirror and towel rail; DN 15/20 complete office water pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
MUT W-13.15 | Excavate and construct septic tank of effective capacity 5.9m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty manhole covers, OD 160 PVC ventilation pipe work with fly screen covers complete and clipped to office wall, include 4 no. manholes from water borne toilet; all to the Engineer's satisfaction | Sum | 1 |  | 0
MUT W-13.16 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to septic tank with OD 160mm PVC drain pipes | nr | 1 |  | 0
MUT W-13.17 | Construct all site storm water drainage works including pipework to road side drain and outfall | Sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT W-13/1 |  |  |  | 0
| Collection, Page MUT W-13/2 |  |  |  | 0
| Collection, Page MUT W-13/3 |  |  |  | 0
| Collection, Page MUT W-13/4 |  |  |  | 0
| Collection, Page MUT W-13/5 |  |  |  | 0
| Collection, Page MUT W-13/6 |  |  |  | 0
| Collection, Page MUT W-13/7 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT ME-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT ME-1
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS DWD 77378
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Borehole Pumps
ME 1.1.1 | Electric multistage centrifigual submersible borehole pumpset with motor, capacity Q = 45.0m3/hr at a head of 149m delivering to Reservoir; complete with starter, delivery pressure gauge, pressure switch, protective controls against dry runs, and all accessories as Grundfos or equal approved | No. | 1 |  | 0
0
ME 1.1.2 | Manufacturer's recommended spares for 3 years operation of 1No. borehole pumps including 1no. spare motor for the pump | Set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Borehole Pump, Guard and Attendant Houses
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 4 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 4 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 3 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 6 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 6 |  | 0
EE 1.2 | Earthing and Lightning Protection
EE 1.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 12 |  | 0
EE 1.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 3 |  | 0
EE 1.2.3 | Test clamp complete as by FURSE or equal. | No. | 3 |  | 0
EE 1.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 3 |  | 0
EE 1.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | M | 20 |  | 0
EE 1.2.6 | 150KVA Electronic stabilizer rated at 400V, 50Hz 3 phase, input voltage +/-25%, output voltage +/-5%, complete with independent phase control, input/output isolators and bypass switch and all accessories as made by Orteo of Italy or equal approved. | No. | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 1.2.7 | Motor Control Centre for borehole incorporating main circuit breaker, starter, controls and protection for pump (HIGH/LOW pressure and dry running), under and overvoltage relay and single phasing relay, power monitor, hour, volt and Amp meters, and all accessories complete as in specifications | No. | 1 |  | 0
EE 1.2.8 | Armoured cable 4corex10mm2 PVC/SWA/PVC laid in conduits to pumps complete | m | 75 |  | 0
Power Supply to Pump House
EE 1.3 | Solar Power
EE 1.3.1 | Supply and Installation of additional mono crystalline PV Solar panels rated at 280pW 12 Volts DC, include: PV solar panel support structure for mounting solar panels; all electrical accessories; to the Engineer's approval | No. | 293 |  | 0
EE 1.4 | Extension of Hydroelectricity Grid
EE 1.4.1 | 33KV line on Creosote treated poles with a guaranteed life of at least 10years, with 3Nox100mm2 AAAC plus earth wire constructed to UMEME standards complete with insulators, stay wires and all accessories. | Km | 1.5 |  | 0
EE 1.4.2 | 150KVA, 3phase, 33KV/433V Dyn11, 50Hz oil filled outdoor, plinth mounted transformer, conservator tank with silica gel breather, Temperature gauge, off-load tap changer, explosion vent, and additional neutral for grounding, protection cage, reinforced concrete plinth, and all accessories all to comply with UMEME Standards. | No | 1 |  | 0
EE 1.4.3 | Allow a Provisional Sum for Utility connections at 33KV, metering unit and connection from UMEME supply to pump control panels | Item | 1 | 30000000 | 30000000
EE 1.4.4 | Allow for profit and overheads on above. | %
EE 1.4.5 | Lockable Meter Box to UMEME approval (400x600x200mm) in 2mm MS Sheets complete with cutouts and all accessories | No. | 1
|  |  |  | Carried to Collection | 30000000
COLLECTION
| Collection, Page MUT ME-1/1 |  |  |  | 0
| Collection, Page MUT ME-1/2 |  |  |  | 0
| Collection, Page MUT ME-1/3 |  |  |  | 30000000
|  |  |  | Carried to Summary | 30000000

## MUT ME-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT ME-2
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (WATER OFFICE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Water Office
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 10 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 8 |  | 0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 5 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 10 |  | 0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 2 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 8 |  | 0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 8 |  | 0
EE 2.1 | Earthing and Lightning Protection
EE 2.1.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 30 |  | 0
EE 2.1.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 4 |  | 0
EE 2.1.3 | Test clamp complete as by FURSE or equal. | No. | 4 |  | 0
EE 2.1.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 4 |  | 0
EE 2.1.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.1.6 | 63A TPN IP65 Isolator. | No. | 2 |  | 0
EE 2.1.6 | 100A TPN IP65 Isolator. | No. | 2 |  | 0
0
|  |  |  | Carried to Collection | 0
EE 2.2 | Power Supply to Water Office |  |  | 0
0
EE 2.2.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT ME-2/1 |  |  |  | 0
| Collection, Page MUT ME-2/2 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT ME-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT ME-3
DESCRIPTION: MECHANICAL & ELECTRICAL WORKS (CHEMICAL HOUSE)
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Chlorine Generation & Dosing Equipment |  |  | 0
0
ME 1.1.1 | Supply and Install DOSATRON D60S model or equivalent in line proportional chemical doser or its equivalent approved by the Engineer including all inlet, outlet, drain, venturi, overflow and interconnection connection pipes to solution tank (PVC, 1") with valves and all accessories with a minimum capacity of 10-60m3/hr | nr | 1 |  | 0
ME 1.1.2 | Manual geared vertical mixers- agitators- propeller 2 blade type, stainless steel shaft, coupling, propeller diameter 600mm, fixed to rigid steel structure complete. | nr | 1 |  | 0
ME 1.1.3 | Rigid steel structure - made of black mild steel double L- profiles; intermediate stands - hot dip galvanized & coated, complete with base plates, anchors, nuts, bolts & washers, etc | nr | 1 |  | 0
ME 1.1.4 | Manufacturer's recommended spares for 3 years operation of dosing pumps | set | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Chemical House
EE 2.1 | Lighting and Small Power
EE 2.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 2 |  | 0
EE 2.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 2 |  | 0
EE 2.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 1 |  | 0
EE 2.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 1 |  | 0
EE 2.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 1 |  | 0
EE 2.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 1 |  | 0
EE 2.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 1 |  | 0
EE 2.2 | Earthing and Lightning Protection
EE 2.2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 20 |  | 0
EE 2.2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 1 |  | 0
EE 2.2.3 | Test clamp complete as by FURSE or equal. | No. | 1 |  | 0
EE 2.2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 1 |  | 0
EE 2.2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | m | 20 |  | 0
EE 2.2.6 | 63A TPN IP65 Isolator. | No. | 1 |  | 0
EE 2.2.6 | 100A TPN IP65 Isolator. | No. | 1 |  | 0
|  |  |  | Carried to Collection | 0
EE 2.3 | Power Supply to Chemical House |  |  | 0
0
EE 2.3.1 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT ME-3/1 |  |  |  | 0
| Collection, Page MUT ME-3/2 |  |  |  | 0
| Collection, Page MUT ME-3/3 |  |  |  | 0
| Cost for 1No. Chemical House |  |  |  | 0
| Total Cost of Chemical Houses | nr | 2 | 0 | 0
|  |  |  | Carried to Summary | 0

## MUT ME-4
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT ME-4
DESCRIPTION: TOOLS AND EQUIPMENT
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Supply of all Office, Plumbing, Mechanical, Electrical, Miscellaneous, Equipment, as detailed in SPECIFICATIONS and summarized below. Supplied Items should be to the Engineer's approval
OFFICE EQUIPMENT
OE 1.1 | Writing desk 1,560 x 780 x 750 mm (L x W x H) with closed front view and 6 lockable drawers | No. | 4 |  | 0
OE 1.2 | Executive swivel, high back tilting steel office chair with arm rests and padded seat and back in black rexine | No. | 1 |  | 0
OE 1.3 | Executive steel office chairs with padded seat and back in black rexine | No. | 3 |  | 0
OE 1.4 | Steel cabinet 1,950 x 950 x 420 mm (L x W x H) with double lockable doors, 4 shelves; colour: grey | No. | 1 |  | 0
OE 1.5 | Lockable steel filing cabinet with 4 drawers | No. | 1 |  | 0
OE 1.6 | Computer Workstation complete as specified | No. | 2 |  | 0
Intel Core i7-2500 3.30GHz, 6M Smart Cache processor
16 GB of DDR 1066 MHz SDRAM; 1TB SATA Hard Disk Drive
16X DVD +/- RW; 17” TFT “Ultra Sharp Flat Panel
Licensed Microsoft Windows 7
Licensed MS Office 2010 & Kaspersky Internet Security 2013
UPS of minimum specification 1500 VA
OE 1.7 | HP Laser Jet Printer | No. | 1 |  | 0
Printer speed- up to 24 ppm black; Processor speed- 533 MHz
Paper trays- 2 trays; Input capacity- Up to 500sheets
Memory- 544MB (512MB DDR SDRAM)
Media size- Max. A4; 10/100 Network Interface Card
5no. Replacement Toner Cartridges
Bi-directional parallel cable; USB printer cable
PLUMBING TOOLS AND EQUIPMENT
PE 2.1 | Blowlamp: pump action, pressure type, approx. 0.5 litre capacity, complete with wind proof nozzle and one set of replacement parts | No. | 2 |  | 0
PE 2.2 | Brushes, wire type for cleaning parts, 300 mm long, 3 rows of approximately15 tufts with 25 mm long steel bristles | No. | 2 |  | 0
PE 2.3 | File, flat machinist's, length 250 mm, second cut | No. | 1 |  | 0
PE 2.4 | File, flat machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.5 | File, flat machinist's, length 250 mm, bastard cut | No. | 1 |  | 0
PE 2.6 | File, half-round machinist's, length 250 mm, smooth cut | No. | 1 |  | 0
PE 2.7 | File, half-round machinist's, length 250 mm, but bastard cut | No. | 1 |  | 0
PE 2.8 | File handles, 100 x 27 mm | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
PE 2.9 | Hammer, mechanic's, 200 & tempered forged steel head, ash or white hickory handle, polished face | No. | 1 |  | 0
PE 2.10 | Precision Level, plumb and spirit, approximately 600 x 25 x 75 mm, varnished beech wood or aluminium, class of accuracy 0.025 mm/m | No. | 1 |  | 0
PE 2.11 | Mattocks | No. | 1 |  | 0
PE 2.12 | Pliers, arc joint, minimum 5 adjustments, 240 mm long | No. | 1 |  | 0
PE 2.13 | Saw, Plumbers, 400 mm, fine tooth edge for cutting metal and coarse teeth for cutting wood, complete with 5No. blades | No. | 1 |  | 0
PE 2.14 | Screw drivers, assorted, hammer-proof, non-inflammable plastic handle | Set | 1 |  | 0
PE 2.15 | Shovels | No. | 1 |  | 0
PE 2.16 | Tape measure, Stanley type steel, metric units, 5 m | No. | 1 |  | 0
PE 2.17 | Tapping machine, furnished with ratchet crank for manual operation, for making tappings from DN 15 (1/2") to DN 50 (2") on mains of DN 25 (1”) to DN 300 (12”) | No. | 1 |  | 0
PE 2.18 | Die set with stock, for threading from DN 15 to DN 150 | No. | 1 |  | 0
PE 2.19 | Vice with parallel jaw 100 mm as Peddinghaus, Matador 10203, portable type, with tripod stand | No. | 1 |  | 0
MECHANICAL TOOLS AND EQUIPMENT
ME 3.1 | 0.5 kg axe. | No. | 1 |  | 0
ME 3.2 | Caliper, precision slide type, metric unit. | No. | 1 |  | 0
ME 3.3 | Carpenter chisel from 6.4 mm to 25.4 mm bevelled edge. | Set | 1 |  | 0
ME 3.4 | Mason chisel from 25.4 mm to 50 mm wide blade. | Set | 1 |  | 0
ME 3.5 | Carpenter's screw clamps, 250 mm opening. | No. | 2 |  | 0
ME 3.6 | Carpenter's screw clamps, 500 mm opening. | No. | 2 |  | 0
ME 3.7 | Square set, metric unit. | No. | 1 |  | 0
ME 3.8 | Crowbars, small, medium, large. | Set | 1 |  | 0
ME 3.9 | Gasket cutter, 600 mm. | No. | 1 |  | 0
ME 3.10 | Dividers. | Set | 1 |  | 0
ME 3.11 | Six assorted files, half round, 250mm, including handles. | Set | 1 |  | 0
ME 3.12 | Spare file handles, 100 x 27 mm. | No. | 5 |  | 0
ME 3.13 | 3 suitable feelers, in tenths of millimetre and 150 mm long. | Set | 1 |  | 0
ME 3.14 | Mechanic's hammer, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.15 | Carpenter's claws 1/5, 1/2. 1 and 2 kg. | No. | 2 |  | 0
|  |  |  | Carried to Collection | 0
0
ME 3.16 | Sledge hammer, 3 kg. | No. | 2 |  | 0
ME 3.17 | Rubber mallet, 1/5, 1/2, 1 and 2 kg. | No. | 2 |  | 0
ME 3.18 | Hooks to remove packings. | No. | 2 |  | 0
ME 3.19 | Grease gun, 200 ml minimum. | No. | 1 |  | 0
ME 3.20 | Oiler, approx. 200 ml capacity, trigger operated, 150mm long flexible spout. | No. | 1 |  | 0
ME 3.21 | Carpenter's pincers, 200 mm jointer's shouldered type. | No. | 2 |  | 0
ME 3.22 | Adjustable pliers, 300 mm and 400mm. | Set | 1 |  | 0
ME 3.23 | Round nose pliers, 150 mm. | No. | 1 |  | 0
ME 3.24 | Puller set, inside-outside, to suit bearings and couplings incorporated in the equipment. | No. | 1 |  | 0
ME 3.25 | Punches, 1 - 10 mm. | Set | 1 |  | 0
ME 3.26 | Reamer, 7 - 17 mm. | Set | 1 |  | 0
ME 3.27 | Hack Saw, adjustable tubular frame, length 250-300mm, including 20 Nos. of spare blades. | No. | 1 |  | 0
ME 3.28 | Sockets, numbers ranging from 2 to 38, with ratchets and handles | Set | 1 |  | 0
ME 3.29 | Scraper spoon, flat and triangular type. | Set | 1 |  | 0
ME 3.30 | Snips, tin plate cutter, 300 mm. | No. | 1 |  | 0
ME 3.31 | Shears, universal, 200 mm. | No. | 1 |  | 0
ME 3.32 | Wrench, chain 16 to 100 mm capacity. | No. | 1 |  | 0
ME 3.33 | Wrench, pipe 300/400/600/900 mm. | No. | 2 |  | 0
ME 3.34 | Wrench, allen set, numbers ranging from 2 to 38. | No. | 1 |  | 0
ME 3.35 | Open ended spanner, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.36 | Ring spanners, 6-24 mm, metric size. | Set | 1 |  | 0
ME 3.37 | Hexagon nut drive spanners, 2-14 mm, metric size. | Set | 1 |  | 0
MISCELLANEOUS TOOLS
MT 5.1 | Contractor's pick axe with point and chisel steel end, length 800 mm | No. | 2 |  | 0
MT 5.2 | Steel hoe, blade width 200 mm, 1.5 kg complete with good wooden handle | No. | 2 |  | 0
MT 5.3 | Seamless pressed tray wheelbarrow, steel frame, with pneumatic wheels, 80 litres | No. | 2 |  | 0
MT 5.4 | Steel Slashers | No. | 5 |  | 0
MT 5.5 | 33CC 2-Cycle Petrol-Powered engine Straight Shaft Attachment Capable String Lawn Trimmer with 17-inch cutting path (including 10No. replacement trimmer lines) | No. | 1 |  | 0
MT 5.6 | Steel rakes | No. | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT ME-4/1 |  |  |  | 0
| Collection, Page MUT ME-4/2 |  |  |  | 0
| Collection, Page MUT ME-4/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## MUT S-1
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT S-1
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - BOYS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 43.4 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 75 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 187 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 12 |  | 0
|  |  |  | Carried to Collection | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT S-1.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
MUT S-1.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
MUT S-1.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
MUT S-1.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
MUT S-1.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
MUT S-1.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
MUT S-1.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
0
MUT S-1.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
MUT S-1.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Water and Drainage
MUT S-1.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
MUT S-1.11 | Construct Urinal facility complete with floor trap, domical removable cast iron grating, gulley trap and including OD 110 uPVC PN 6 drainage pipework to soak away pit | sum | 1 |  | 0
MUT S-1.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
MUT S-1.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
MUT S-1.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
MUT S-1.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT S-1/1 |  |  |  | 0
| Collection, Page MUT S-1/2 |  |  |  | 0
| Collection, Page MUT S-1/3 |  |  |  | 0
| Collection, Page MUT S-1/4 |  |  |  | 0
| Collection, Page MUT S-1/5 |  |  |  | 0
| Collection, Page MUT S-1/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## MUT S-2
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT S-2
DESCRIPTION: 5 STANCE VIP SCHOOL LATRINES - GIRLS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 70 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
|  |  |  | Carried to Collection | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.45 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
G813 | Terrazo floor finish | m² | 20.3 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 77 |  | 0
|  |  |  | Carried to Collection | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 80 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 193 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 13 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT S-2.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 6 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
MUT S-2.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
MUT S-2.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
MUT S-2.4 | Supply and complete installation of corrosion proof manhole access covers 1000mm x 900mm complete as specified including lifting hooks | nr | 5 |  | 0
Roofing
MUT S-2.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
MUT S-2.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
MUT S-2.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
MUT S-2.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
MUT S-2.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
MUT S-2.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
MUT S-2.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
MUT S-2.12 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm dia chromium plated pillar taps | nr | 1 |  | 0
MUT S-2.13 | Provide materials and construct a 2no. tap hand washing tap stand complete with DN 13mm GI pipework, uPVC drainage pipework, all fittings, DN 13mm taps, waste outlet grating, all accessories; as per specifications and drawings and to the Engineer's approval | nr | 1 |  | 0
MUT S-2.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
MUT S-2.15 | Supply and Install OD 110 mm uPVC PN 6 pipework to BS 4660, complete with spigot and socket joints, all fittings; from hand washing tap stand and urinal trough to Soak Pit | m | 12 |  | 0
MUT S-2.16 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
MUT S-2.17 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT S-2/1 |  |  |  | 0
| Collection, Page MUT S-2/2 |  |  |  | 0
| Collection, Page MUT S-2/3 |  |  |  | 0
| Collection, Page MUT S-2/4 |  |  |  | 0
| Collection, Page MUT S-2/5 |  |  |  | 0
| Collection, Page MUT S-2/6 |  |  |  | 0
| Cost for 1No. Toilet Block |  |  |  | 0
| Total Cost of Toilet Blocks | nr | 1 | 0 | 0
|  |  |  | Carried to Summary | 0

## MUT S-3
MINISTRY OF WATER AND ENVIRONMENT
INTEGRATED WATER MANAGEMENT AND DEVELOPMENT PROJECT
MUTUNDA RGC PIPED WATER SUPPLY AND SANITATION SYSTEM
BILL No. MUT S-3
DESCRIPTION: 4 STANCE PUBLIC WATERBORNE TOILETS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | m2 | 110 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 37.6 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E323 | Depth 0.5 - 1 m | m³ | 37.2 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to toilet block and compacted to 98% MOD AASHTO | m³ | 5.2 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 4.2 |  | 0
E647 | 200mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 16.5 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 42 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 2.5 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F251 | 10mm aggregate | m³ | 8.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete for footings, grade C15 of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 2.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F522 | Thickness 150-300mm | m³ | 4.7 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C20, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 3 |  | 0
Beams
Placing reinforced concrete, grade C20, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 0.7 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.4 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 9.6 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | kg | 150 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 28.3 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 17.7 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 200 mm thick | m² | 47 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 21 |  | 0
|  |  |  | Carried to Collection | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 4 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 67 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 5.7 |  | 0
Masonry
External quality weather guard paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 49 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 79 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153.1 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 78.1 |  | 0
W153.2 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a steel float | m² | 49 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 78.1 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.3 |  | 0
|  |  |  | Carried to Collection | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 16.5 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 49 |  | 0
MISCELLANEOUS WORKS
Structural
Windows
Supply and fix the following mild steel windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, stays, plugging and fixing to wall
MUT S-3.1 | Top hung double leaf hinged windows overall size 3450 x 1150mm high comprising of 3mm thick mild steel panes welded on a 25x25x3mm thick angle frame and epoxy coated colour blue | nr | 1 |  | 0
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
MUT S-3.2 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
MUT S-3.4 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
MUT S-3.5 | Single leaf door overall size 1000 x 2100mm high | nr | 3 |  | 0
Roofing
MUT S-3.6 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, metal lathe ceiling and eaves, and all roofing timber, gauge 26 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 34.7 |  | 0
Building Finishes
MUT S-3.7 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
MUT S-3.8 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
MUT S-3.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 10no. toilet paper holders, installation of floor drains with associated pipework and fitting s connected to soak pit, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Water and Drainage
MUT S-3.10 | Supply and erect 1000 litre (1m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
MUT S-3.11 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
MUT S-3.12 | Construct Urinal facility with perforated DN 20 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap | sum | 1 |  | 0
MUT S-3.13 | Construct Shower Closet with DN13 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap, elevated perforated circular shower head, 13mm diameter chromium plated pillar taps | sum | 1 |  | 0
MUT S-3.14 | Provide materials and construct a hand washing facility complete with wash hand basins, DN 13/20 GI/PPR plumbing pipework, uPVC drainage pipework, all fittings, gulley and bottle traps, valves, 13mm diameter chromium plated pillar taps, waste outlet gratings, all accessories, including single low level wash hand basin for disabled person's usage; as per specifications and drawings and to the Engineer's approval | nr | 2 |  | 0
MUT S-3.15 | Excavate and construct standard manholes in 200mm thick blockwork, internal depth not exceeding 1.0m, bonded in concrete mortar(1:5) and rendered internally with concrete mortar (1:4), concrete benching, complete with and including CI frame and cover, and interconnecting OD 110mm pvc drain pipes to toilet block | nr | 4 |  | 0
MUT S-3.16 | Supply and Install OD 110 mm uPVC PN 6 drainage pipework to BS 4660, complete with spigot and socket joints, all fittings; from toilet block to Septic Tank and Soak Pit | m | 78 |  | 0
MUT S-3.17 | Excavate and construct Septic Tank of effective capacity 15.4m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty cast iron manhole covers | Sum | 1 |  | 0
MUT S-3.18 | Excavate and construct 2500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
MUT S-3.19 | Supply and install squatting type low level water closet suite complete with WC pan, heavy duty cistern complete with anti-vandal cage, flush pipe, connected to nearest manhole; all to the Engineer's satisfaction | nr | 3 |  | 0
MUT S-3.20 | Supply and install seat type low level water closet suite complete with WC pan, heavy duty cistern, flush pipe complete with anti-vandal cage, connected to nearest manhole; all to the Engineer's satisfaction | nr | 2 |  | 0
MUT S-3.31 | Allow for the construction of an incinerator block at the school premise as directed by the Engineer | sum | 1 |  | 0
| Power Supply to Waterborne Toilet |  |  | 0
0
MUT S-3.32 | Provision for Supply and Installation of a solar powered system inclusive of power storage batteries, controls and all accessories to the Engineers satisfaction | Item | 1 |  | 0
0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page MUT S-3/1 |  |  |  | 0
| Collection, Page MUT S-3/2 |  |  |  | 0
| Collection, Page MUT S-3/3 |  |  |  | 0
| Collection, Page MUT S-3/4 |  |  |  | 0
| Collection, Page MUT S-3/5 |  |  |  | 0
| Collection, Page MUT S-3/6 |  |  |  | 0
|  |  |  | Carried to Summary | 0